GOVERNMENT OF PAKISTAN

MINISTRY OF INDUSTRIES & PRODUCTION

Islamabad, the   November, 2010.

NOTIFICATION

S.R.O.       (I)/2010.- In exercise of the powers conferred by section 4, sub-section (2) of section 5, sub-section (2) of section 14, sections 21 and 22 and sub-section (1) of section 29 of the Petroleum Act, 1934 (XXX of 1934), the Federal Government is pleased to make the following rules, the same having been previously published vide Notification No. S.R.O. 104(KE)/2010, dated the 2nd August, 2010, as required under sub-section (2) of section 29 of the said Act, namely:-

In the aforesaid Rules,-

- in rule 30, in sub-rule (2), for the figures “500” and “100”, the figures “5000” and “1000” shall be substituted respectively;

- in rule 77,-

(a) for the marginal note, the following shall be substituted, namely:-

“License for vehicle to transport petroleum, compressed natural gas, 	liquefied petroleum gas, liquefied natural gas, industrial compressed gases in 	bulk.-”; and

(b) for sub-rules (1), (1A), (1B) and (1C), the following shall be substituted, 	namely:-

“(1) The petroleum including compressed Natural Gas, Liquefied Petroleum Gas, Liquefied Natural Gas, Industrial Compressed Gases shall not be transported by road without license granted by Chief Inspector of Explosives or Inspector of Explosives authorized by Chief Inspector of Explosives. After physical inspection of vehicle and scrutiny of requisite particulars which shall be furnished together with an original treasury receipt duly paid according to S. Nos. 12, 13, 14 and the corresponding entries relating thereto in column (5) of Schedule-I:

Provided that this rule shall not be apply to the tank or cylinder fitted in the vehicle for fueling.”;

(3)	after rule 98, the following new rule shall be inserted, namely:-

“98A. Approval of ancillary facilities.- The pump premises, for approval of ancillary facilities, shall conform to the minimum standards as laid down in Schedule IV to these rules.”;

(4)		in rule 103,-

(a)	in sub-rule (3), for the word “hundred”, occurring twice, the word 	“thousand” shall be substituted; and

(b)	for the word “fifty”, the words “seven hundred and fifty” shall be 	substituted;

(5)		in rule 114, after sub-rule (2), the following new sub-rule shall be added, namely:-

“(3) 	Scrutiny fee of five hundred rupees (not refundable) shall be payable 	with each such application for grant or renewal of a license.”

(6)		in rule 118, in sub-rule (3), for the words “twenty five rupees” the words “equal to 	license fee” shall be substituted;

(7)		in rule 119, after sub-rule (3) the following new sub-rule shall be added, namely:-

“(4) Fresh license, in lieu of the expired license, shall be granted only on payment of three times the fee ordinarily payable for the license plus fee, equal to the license fee, for each year or part thereof  which the license remained expired.”;

(8)	in rule 120, in sub-rule (2), for the word “twenty-five”, the words “five hundred” shall be substituted;

(9)	in rule 121, in sub-rule (3), for the word “twenty-five” the words “five hundred” shall be substituted;

(10)	in rule 122, after sub-rule (2), the following new sub-rule shall be added, namely:-

“(3) Every such appeal shall be accompanied by a scrutiny fee of three thousand rupees (non-refundable), if preferred to Chief Inspector, and five thousand rupees if preferred to the Federal Government. No such fee is required for the appeal specified in clause (ii) of sub-rule (1).”;

(11)	in rule 125, for sub-rule (3), the following shall be substituted, namely:-

“(3) A fee of ten thousand rupees or equal to the license fee, whichever is higher, shall be charged on each such application.”;

(12)	in rule 126, in sub-rule (2), for the words “equal to the license fee” the words “of ten thousand rupees” shall be substituted;

(13)	in rule 127, for the words “of fifteen rupees,” the words “equal to license fee” shall be substituted;

(14)	in rule 130, for sub-rule (2), the following shall be substituted, namely:-

“(2) Copies of any license may, for the purpose of this rule, be authenticated by the licensing authority on payment of one thousand rupees for each authentication. Duplicate   authenticated copy may be issued on payment of five hundred rupees for each license.”;

(15)	in rule 132, after sub-rule (2), the following new sub-rule shall be added, namely:-

“(3) In addition to the storage fee, a scrutiny fee of twenty-five thousand rupees (not refundable) shall be charged for each such application.”;

(16)	in rule 162, in sub-rule (2), for the word “twenty-five”, the words “one thousand” shall be substituted;

(17)	in rule 163,-

(a)	in sub-rule (1), for the word “twenty five” the words “one thousand” shall be substituted; and

(b)	in sub-rule (2), for the figures “200”, “50” and “50”, the figures “2000”, “1000” and “1000” shall be substituted respectively;

(18)	in rule 164,-

(a)	in sub-rule (1),-

(i)	for the word “hundred”, the word “thousand” shall be substituted; and

(ii)	in the proviso, for the figure “1000”, the figure “5000” shall be substituted; and

(b)	in sub-rule (2), for the word “hundred”, the word “thousand” shall be substituted;

(19)	for Schedule I, the following shall be substituted, namely:-

“Schedule-I

[See rule 77(1) and 115]

| Article No. | Form of License | Purpose for which granted | Authority empowered to grant license | Fee |
| --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) |
| 1 2 3 4 5 6 7 8 9 10 11 12 13 14 | Form H, See Schedule-II Form I, See Schedule-II Form J, See Schedule-II Form K, See Schedule-II Form L, See Schedule-II Form M, See Schedule-II Special Form Form B-I Form N Form O Form P Form Q Form R Form S, See Schedule-II | To import dangerous petroleum other than petroleum which can be used in an internal combustion not exceeding 270 liters at any one time. To store dangerous petroleum other than petroleum which can be used in an internal combustion not exceeding 270 liters at any one time. To store non-dangerous petroleum (Kerosene Oil, light diesel oil) other than petroleum which can be used in vehicle for fuel otherwise than bulk, in quantity not exceeding 10,000 liters (in drums). To store petroleum in a tank or tanks in connection with a dispensing unit for fuelling motor conveyances. To import dangerous petroleum and to store petroleum in installations (Bulk Depots and in industries for self consumption. To import and store dangerous petroleum otherwise than in bulk and to store otherwise than in bulk (a) non-dangerous petroleum in quantity exceeding 25,000 liters or (b) partly dangerous petroleum and partly non-dangerous petroleum. To import dangerous petroleum and to store petroleum (in cases not provided for in Articles 1, 2, 3, 4, 5, and 6.) To manufacture/store/sale and dispense compressed natural gas in connection with dispensing unit for fueling motor conveyances only. To store and sale liquefied petroleum gas in a tank or tanks & dispense liquefied petroleum gas in connection with a dispensing unit for fueling motor conveyances. To import/store/sale liquefied petroleum gas in installation (Plants) for filling in cylinders. To store liquefied petroleum gas of quantity exceeding to 100 liters for self use in industries and other places. License to transport petroleum product in bulk on land by mechanically propelled vehicle. License to transport liquefied petroleum gas in bulk on Land by mechanically propelled vehicle. License to transport compressed natural gas in bulk on Land by mechanical propelled Vehicle. (Compressed natural gas storage cylinder mounted in vehicle for fueling are exempted). | The District Authority The District Authority The District Authority. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. | Rs. 5,000/- Rs. 5,000/- Rs. 5,000/- (i) Fee for storage/dispensing of Dangerous Petroleum products Facility is Rs. 5,000/- (ii) Fee for storage/dispensing of Heavy petroleum products (High speed Diesel Oil) facility is Rs. 5,000/- (i) Fee for the storage of Dangerous Petroleum products (Petrol, solvent oil etc.) is Rs. 15,000/- (ii) Fee for the storage of Non dangerous petroleum (Kerosene Oil, Light Diesel Oil) Non-dangerous petroleum products Having the flash point above 76Fº and below 129Fº is Rs. 15,000/- (iii) Fee for storage of heavy petroleum product (High Speed Diesel Oil, Furnace Oil etc) Heavy petroleum having the flash point 129Fº and below 200Fº Rs. 15,000/- Rs. 5,000/- Rs. 5,000/- Rs. 20,000/- Rs. 20,000/- Rs. 25,000/- Rs. 5,000/- Rs. 1,000/- Rs. 5,000/- Rs. 10,000/-”; |

(20)	in Schedule-II,-

(a)	after Form B, the following new Form shall be inserted, namely:-

“FORM ‘B-I

(Article 8 of schedule I)

LICENSE TO MANUFACTURE/STORE/SALE & DISPENSE COMPRESSED NATURAL GAS INCONNECTION WITH DISPENSING UNIT FOR

FUELING MOTOR CONVEYANCES ONLY.

No:			                                                                                                              Fee

Licence is hereby, granted to _________________________________________, To manufacture/store/sale & dispense compressed natural gas in connection with dispensing unit for fueling motor conveyances only at the premises described below and shown in the plan attached here to subject to the provisions of the Petroleum Act, 1934 and the Petroleum Rules, 1937. Safety and Mineral Gas Rules, 1960, made there under and to the further conditions prescribed on the back of this Licence.

Total capacity of gas storage units at S.T.P is-cubic meter of gas or ------------- water liters capacity of cylinders/tanks (s).

This Licence shall remain in force till the 31st day of December.

Licencing Authority				                            Chief Inspector of Explosive in Pakistan

The:

Plan No.                                                      Dated:

Description of the licensed premises referred to above. ________________________________

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

This Licence is liable to be canceled if the Licence premises when inspected is not found confirming to the description and condition attached here to and contravention of any of the rules and conditions under which this Licence is granted is also punishable with fine which may extended to fifteen thousand rupees or with simple imprisonment which may extended to one month or with both for a first offence and fine which may extended to twenty-five thousand rupees or with simple imprisonment which may extended to three months or with for any subsequent offence.

##### CONDITIONS OF LICENCE

- All design, specifications, standards and construction of Gas tanks, Cylinders, Compressor and Fuelling Station shall fulfill the requirements of Code of practice issued by the Pakistan Standard Institution or any other Code approved by the Chief Inspector.

- Tanks, cylinders gas holders and regulating equipments used at the premises shall be located outdoors unless otherwise specially approved.

- A group of gas cylinders shall be linked by piping to from a single gas storage unit.

- CNG Storage unit (s) shall be at least three (3) meters away from footpath and five (5) meters away from CNG or Petroleum filling point.

- CNG Storage unit (s) shall be provided with security fence at least 1 meter away from the cylinder banks.

- Every CNG storage unit including manifold group of cylinders or bulk storage tank shall be provided with suitable pressure gauge.

- Where more than one CNG units are installed, the separating distance between the units shall not be less than two (2) meters.

- CNG dispensing point shall be at least 4.5 meters away from footpath or public place three (3) meters away from the nearest petroleum dispensing unit and 2 meters from any opening into a building.

- Every CNG system shall be fitted with a device to prevent the cylinder being charged with a pressure greater than the cylinder test pressure.

- CNG storage unit (s) shall be provided with isolating valves and master shut-off valve.

- Emergency and isolating shutoff valve shall be provided near CNG refueling bays in easy accessible position. Each flexible hose for refueling vehicle(s) shall be provided with shut-off valve.

- Compressor room shall be ventilated properly at lower level.

- Natural gas shall not be vented to the atmosphere unless the vent is led to a safe point of discharge.

- The inlet gas line to a CNG compressor shall be provided with a non-return valve to prevent back flow in the event of compressor malfunction.

- An effective drying system shall be provided to ensure that moisture is absorbed from the gas prior to its compression.

- All electrical wiring, equipment within hazardous area shall comply with the requirements of BS 4683, BS 229 and BS 4137.

- Gas detector operated cut-out switch shall be fitted to the electrical system of compressor to switch off the unit automatically in the event of a major gas leak.

- A licensing shall not make any alteration, addition or extension of his works without prior approval in writing of the licensing authority.

- If the licensing authority calls upon the holder of a licence by a notice in writhing execute any repairs of the equipment etc. which are in the opinion of such authority, necessary for the safety of the premises, then holder of the licence shall execute the repairs within such period, not being less than one month from the date of receipt of the notice, as may be fixed by the notice.

- The premises shall be posted prominently at the entrances of compressor room.

- A “NO SMOKING” sign shall be posted prominently at the entrance of compressor room.

- There shall be no smoking within six (6) meters of the vehicle.

- Filling instruction shall be posted in a conspicuous place adjacent to the dispensing hose.

- Any accident involving loss of life or serious injury or severe damaged to property shall be immediately reported to the Chief Inspector of Explosive and the nearest Police Station by the quickest means of number shall be furnished with the report.

- Free access to the licensed premises shall be given at all reasonable times to the Chief Inspector of Explosives or Office authorized in this behalf for ascertaining that rules and conditions of the licence are duly observed.”; and

(b)	after Form M, the following new Forms shall be added, namely:-

“FORM  N

[Article 9 of Schedule I]

To store and sale liquefied petroleum gas in a tank or tanks & dispense liquefied petroleum gas in connection with a

dispensing unit for fueling motor conveyances.

License No. _____________________                                               Fee Rs. ________________

License is hereby granted to ___________________________________________valid

for storage of ________________________kilograms of liquefied petroleum gas in __________________ numbers pressure vessels in the premises described below and dispensing of liquefied petroleum gas as automotive fuel to motor vehicles, subject to the provisions of the Petroleum Act 1934 and the made their under.

The license shall remain in force up to 31ST December__________________________                  the __________________ (Date if Issue).

Chief Inspector of Explosives

DESCRIPTION OF LOCATION AND FACILITIES OF THE LICENSED PREMISES

The licensed premises, the layout, boundaries and other particulars of which are shown

in the attached approved plan No. ________________dated _____________are situated at

(address)_________________________________________________________and consists of:-

(i) Storage vessels______________________________________________________________

(Identification number and water capacity) (Specify whether aboveground, mounded or            underground).

ii) Number of dispensers____________________ make________________

iii) other facilities _________________________

SPACE FOR ENDORSEMENT OF RENEWALS

| Date of Renewal | Date of Expiry | Signature and Office Stamp of the Licensing Authority |
| --- | --- | --- |

The license shall be renewable without any concession in fee for one year in the absence of contravention of the provisions of the Petroleum Act 1934 and the rules made their under, or of any of the conditions of the license.

This license is liable to be cancelled if the licensed premises are not found confirming to the description and conditions attached hereto and for contravention of any of the rules and conditions under which this license is granted. The holder of this license is also liable for punishment under Petroleum Act 1934 for the contraventions of the provisions of the said Act and the rules framed there under.

CONDITIONS

1. The licensed premises shall conform to the description of location and facilities and to     the approved plan, as mentioned on the body of the license.

2. The licensed premises shall be used only for the purpose it is licensed for.

3. Liquefied petroleum gas shall be stored only in one or more pressure vessels installed

aboveground, underground or aboveground covered with earth (mound) as per provisions of these rules.

4. Liquefied petroleum gas storage vessel, dispenser, pumps compressor, piping and

other fittings shall be of a design suitable for commercial propane.

5. Storage vessels shall not be installed within any building or shed.

6. A hard stand for parking the tank-truck for the purpose of unloading liquefied

petroleum gas into the storage vessels shall be provided as per rules.

7. The facilities and equipments of the licensed premises shall meet the safety distance

requirements as specified in the rules/standards in matter.

8. Liquefied petroleum gas shall be dispensed only into those cylinders used as fuel

tanks of motor vehicles, which are duly approved by the Chief Inspector, and have

passed the periodic statutory tests under Gas Cylinders Rules, conducted by a testing

station recognized by the Chief Inspector.

9. The type of the dispenser used for dispensing liquefied petroleum gas shall conform

to a specification approved by the Chief Inspector.

(a) It shall be provided with an excess flow valve, a remote operated shut-off valve

and pipe shear provision in the liquid inlet pipe.

(b) The dispenser shall be installed on a firm foundation and protected against

physical damage.

(c) A breakaway device with excess flow valves or quick  action cut-off valves on

both sides of the breakaway device conforming to Underwriters Laboratory USA,

specification no 567 or equivalent shall be provided on the delivery line from the

dispenser before the connection of the hose so as to prevent spillage of liquefied

petroleum gas from both sides of the breakaway point in the event of its breakage.

10. The design pressure of the hose for delivery of liquefied petroleum gas by dispenser to motor vehicles shall be minimum thirty two kilograms per square centimeter with a safety factor of five and shall be tested at one and half times the design pressure at an interval not exceeding every one year. The hose shall be mechanically and electrically continuous. The length of the hose shall not exceed five meters and fifty centimeters.

11. The dispensing nozzle at the end of the hose shall be self sealing type of twenty two

millimeters nominal size and suitable for matching with filling connection of cylinders fitted to vehicles as fuel tanks, as specified in Australian Specification AS-1425 or equivalent standard approved by the Chief Inspector.

12. Clearly identified switches or circuit breakers shall be provided at easily accessible location minimum six meters away from dispenser to cut-off the power supply in the event of fire, accident or other emergency. The switches or circuit breakers shall be visible from the point of dispensing liquefied petroleum gas to motor vehicles.

13. Pump used for pumping liquefied petroleum gas shall be of either centrifugal submersible or positive displacement type. Positive displacement pump shall be provided with bye-pass to prevent over-pressure.

14. Hazardous area classification for the dispenser shall be as under :-

(a) Entire space with in the dispenser enclosure cabinet and forty six centimeters

horizontally from the exterior of enclosure cabinet and up to an elevation of one

hundred and twenty one centimeters above dispenser base and the entire pit or

open space beneath the dispenser shall be Division-1.

(b) Up to forty six centimeters vertically above the surrounding ground level and

horizontally beyond forty six centimeters up to six meters on all sides of the

dispenser enclosure cabinet shall be Division-2.

15. All metallic liquefied petroleum gas piping shall be rated for Propane and designed to American Standard ASME-B-31.3 with minimum design pressure of thirty two kilograms per square centimeters with a factor of safety of four . The materials of pipe shall be low carbon or alloy steel conforming to American Standard ASTM-SA-333, grade, 6, or SA-106, Grade-B-Schedule 80; or API-5L or equivalent. The pipeline shall be tested at one and half times of the design pressure, if hydro-tested. Joints of pipeline above forty millimeters diameter shall be welded or flanged. Threaded or screwed connection shall not be provided except for special fittings like excess flow valve, pump connection upto fifty millimeters diameter.

16. No addition or alteration in the licensed premises shall be carried out without prior sanction of the licensing authority.

17. No person shall enter or cause to repair or repair either by the use of fire, welding, hot riveting or brazing any vessel used for the storage of flammable gas unless it has been thoroughly cleaned and gas-freed or otherwise prepared for safely carrying out such hot work and certified in writing, by a competent person, to have been so prepared. Where the vessel has been certified as gas free, the certificate shall be preserved by the licensee for a period of not less than six months and produced to the Chief Inspector, on demand.

18. The operation of the licensed premises shall be under the supervision of a person having knowledge of the equipments, used in the premises and trained in handling compressed gas, and other operators shall be conversant with the hazards associated with the compressed gas and fire fighting operations.

19. Liquefied petroleum gas shall not be removed from the vessel except by means of   transfer facilities shown in the approved plan attached to the license.

20. Smoking, naked lights, lamps source of fire or any other stimulant capable of igniting flammable vapors shall not be allowed inside the premises.

21. The vessel shall not be filled between the hours of sunset and sunrise, except in such manner and under such other condition or conditions as are specifically endorsed on the license by the licensing authority.

22. All electrical equipment such as motors switches, starters, etc, used for transfer of liquefied petroleum gas shall be of flameproof construction conforming to standard/type approved by Chief Inspector.

23. Every person managing or employed on or in connection with license premises shall abstain from any act whatsoever which tends to cause fire or explosion and which is not reasonably necessary and to the best of his ability, shall prevent any other person from doing such act.

24. At least two numbers of nine kilograms capacity dry chemical type fire-extinguishers shall be provided near the tank-truck unloading area and one number similar extinguisher shall be provided near each dispenser and transfer pump location. In dispensing station having aboveground liquefied petroleum gas storage vessels, hydrants with minimum water pressure of seven kilograms per square centimeters shall be provided at convenient positions for all-round coverage of liquefied petroleum gas storage vessels, and handling area and water sprinklers with a spray density of ten liters per minute per square meter shall be provided. The fire water pump shall be preferably diesel engine driven, with capacity to deliver water at the rate and pressure specified above. The minimum fire water storage at the premises shall be needed for fighting fire at least for one hour.

25. During the period of unloading of liquefied petroleum gas from tank-truck to the storage vessels dispensing operation to vehicles shall not be carried out.

26. The emergency telephone numbers of local fire service, police and the principal marketing company, and emergency instructions shall be conspicuously displayed in the licensed premises.

27. All valves on the vessel and pipelines in the premises must be permanently marked in a manner clearly indicating the direction of opening and closing.

28. If the licensing authority calls upon the holder of a license by a notice in writing to execute any repairs in the licensed premises which are, in the opinion of such authority, necessary for the safety of the premises, the holder of the license shall execute the repairs within such period as may be specified in the notice.

29. Any accident, fire or explosion within the licensed premises which is attended with loss of life or serious injury to person or property shall be immediately reported to the nearest Judicial Magistrate or to the officer-in-charge of the nearest police station and to the Chief Inspector of Explosives by telephone/fax.

30. Free access to the licensed premises shall be given at all reasonable times to any of the officers specified in rule in the matter, and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed.

FORM ‘O’

[Article 10 of Schedule I ]

Licence to import/store/sale liquefied petroleum gas in installation (Plants) for filling in cylinders.

No. …………………							Fee Rs. ……………………

License is hereby granted to……………………………………………valid only for import/store/sale liquefied petroleum gas in installation (Plants) for filling in cylinders for the storage of …………………water liters liquefied petroleum gas in the place described below and shown on the plan attached hereto subject to the provisions of the petroleum Act, 1934 and the rules made there under and to the further condition on the back of this license.

This license shall remain in force till the 31st day or December 20 …………

| Sr. No. | Nature of Petroleum to be stored/imported | Quantity of petroleum (In liters) |
| --- | --- | --- |
| 1. | Liquefied petroleum gas in bulk. |  |
| 2. | Liquefied petroleum gas not in bulk. |  |
|  | Total |  |

Chief Inspector of Explosives

Plan No. …………………………dated …………

Description of the place referred to above

…………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………..

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed premises, when inspected, are not found conforming in the description approved plan by Department of Explosives and conditions attached hereto and contravention of any of the rules and conditions under which this is granted is also punishable with fine may extend to ten thousand rupees for a first offence and may extend to twenty thousand rupees for any subsequent offence.

CONDITIONS

1. The licensed premises shall not be used for any purpose other than storage and transfer of  compressed gas and purposes directly connected therewith.

2. The compressed gas shall be stored only in one or more vessels of capacity………cubic

meters………Kg. and in position shown in the approved plan attached hereto.

3. Every vessel shall be outside any building and shall be supported on well designed

foundations.

4. The storage vessel shall at all times maintain from any other facility, building, boundary,

fencing or protected works the distances specified rules/standards in the matter.

5. A suitable hard stand for parking of the vehicle during loading or unloading of any compressed gas shall be provided. The following minimum safety distances shall be provided between the centre of the hard stand and the storage vessel or boundary line of installation; as well as between the loading or unloading points and storage vessel or boundary line of installation, -

i)    as per  rules/standards in the matter, as the case may be, in case of refinery, terminal and cylinder filling plants for flammable liquefied gases;

ii)   four meters and fifty centimeters in case of non-corrosive, non-toxic and non-flammable  gases; and

iii)  nine meters in all other cases.

6. All fitments of the vessel shall be well maintained.

7.  No alteration of the position of the vessel and no replacement of the vessel shall be effected except the previous sanction, in writing, of the licensing authority. All alterations so sanctioned under this condition shall be shown on an amended plan to be attached to the license.

8. If the licensing authority calls upon the holder of a license by a notice in writing to execute any repairs in the licensed premises which are, in the opinion of such authority, necessary for the safety of the premises, the holder of the license shall execute the repairs within such period of as may be specified in the notice.

9. Every vessel before being repaired or exhumed shall be made free of compressed gas and thoroughly cleaned. When a vessel is opened for cleaning or repairs, no lamp of any description either ordinary of electric, electric cables or fans and no articles, appliances or equipment capable of igniting flammable, vapors shall be brought near the vessel.

10. No person shall cause to repair or repair either by the use of fire, welding, hot riveting or brazing any vessel used for the storage of flammable gas unless it has been thoroughly cleaned and gas-freed or otherwise prepared for safely carrying out such hot work and certified in writing, by a competent person, to have been so prepared. Where the vessel has been certified as gas-free, the certificate shall be preserved by the licensee for a period of not less than three months and produced to the Chief Inspector, on demand.

11. No person shall enter any vessel used for the storage of a toxic or corrosive gas unless he is adequately protected by means of clothing, gas masks and such other protective equipment.

12. Compressed gas shall enter the vessel through sound pipes having no leaks at any place.

13. The vessel shall not be filled between the hours of sunset and sunrise, except in such manner and under such other condition or conditions as are specifically endorsed on the license by the licensing authority.

14. No artificial light capable of igniting flammable vapors shall at any time be present within 9 meters of the vehicle and the loading or unloading points during the transfer of the compressed gas and no person engaged in such transfer shall smoke.

15. No compressed gas shall be removed from the vessel except by means of transfer facilities marked in the plan attached hereto.

16. All electrical equipment such as motors switches, starters, etc., used for transfer of flammable compressed gas shall be of flameproof construction conforming to approved specifications.

17. Every person managing or employed on or in connection with the licensed premises shall abstain from any act whatsoever which tends to cause fire or explosion and which is not reasonably necessary and to the best of his ability, shall prevent any other person from doing such act.

18. The licensee shall provide for each licensed premises a minimum of two portable foam types or dry chemical type fire extinguishers of 9 Kgs. capacity each, which shall be kept ready at convenient location for immediate use in the event of any fire.

19. Except for necessary pipes and valves and approved electric lights the space within the licensed premises shall be kept entirely clear and unoccupied.

20. All valves in the premises must be permanently marked in a manner clearly indicating the direction of opening and shutting the valve.

21. Any accident, fire or explosion within the licensed premises which is attended with loss of life or serious injury to person or property shall be immediately reported to the nearest Judicial Magistrate or to the officer in charge of the nearest police station and by telephone to the Chief Inspector of Explosives.

22. Free access to the licensed premises shall be given at all reasonable times to any of the Inspector of Explosives and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed.

(ii)	All metal pipes shall be flexible pipes shall be tested once every 6 months by a competent engineer holding license to ascertain fitness and compliance with the requirement of strength laid down above.

(iii)	(a) 	A complete and permanent record of such testing shall be maintained in the licensed premises.

(b) 	The date of the last test shall be recorded on the pipes and pipe section concerned in a distinctive manner.

23.	The license shall not deliver from the licensed premises:-

  - Petroleum in bulk to any vessel used in the carriage of petroleum in bulk by water; and

  - Any petroleum in bulk shall be delivered to any vehicle used for the transport of petroleum in bulk by road unless such vehicle is licensed by the Chief Inspector.

FORM ‘P’

[Article 11 of Schedule I ]

LICENCE TO STORE LIQUEFIED PETROLEUM GAS OF QUANTITY EXCEEDING TO 100 LITERS FOR SELF USE IN INDUSTRIES AND OTHER PLACES.

No. …………………							Fee Rs.  ……………………

License is hereby granted to……………………………………………valid only for store liquefied petroleum gas of quantity exceeding to 100 liters for self use in industries and other places for the storage of …………………water liters liquefied petroleum gas in the place described below and shown on the plan attached hereto subject to the provisions of the petroleum Act, 1934 and the rules made there under and to the further condition on the back of this license.

This license shall remain in force till the 31st day or December 20 …………

| Sr. No. | Nature of Petroleum to be stored/imported | Quantity of petroleum (In liters) |
| --- | --- | --- |
| 1. | Liquefied petroleum gas in bulk |  |

Chief Inspector of Explosives

Plan No. …………………………dated …………

Description of the place referred to above …………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………..

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed premises, when inspected, are not found conforming in the description approved plan by Department of Explosives and conditions attached hereto and contravention of any of the rules and conditions under which this is granted is also punishable with fine may extend to ten thousand rupees for a first offence and may extend to twenty thousand rupees for any subsequent offence.

CONDITIONS

1. The licensed premises shall not be used for any purpose other than storage and transfer of compressed gas and purposes directly connected therewith.

2. The compressed gas shall be stored only in one or more vessels of capacity………cubic

meters………Kg. and in position shown in the approved plan attached hereto.

3. Every vessel shall be outside any building and shall be supported on well designed

foundations.

4. The storage vessel shall at all times maintain from any other facility, building, boundary,

fencing or protected works the distances specified rules/standards in the matter.

5. A suitable hard stand for parking of the vehicle during loading or unloading of any compressed gas shall be provided. The following minimum safety distances shall be provided between the centre of the hard stand and the storage vessel or boundary line of installation; as well as between the loading or unloading points and storage vessel or boundary line of installation,-

i)    as per  rules/standards in the matter, as the case may be, in case of refinery, terminal and cylinder filling plants for flammable liquefied gases;

ii)   four meters and fifty centimeters in case of non-corrosive, non-toxic and non-flammable  gases; and

iii)  nine meters in all other cases.

6. All fitments of the vessel shall be well maintained.

7.  No alteration of the position of the vessel and no replacement of the vessel shall be effected except with the previous sanction, in writing, of the licensing authority. All alterations so sanctioned under this condition shall be shown on an amended plan to be attached to the license.

8. If the licensing authority calls upon the holder of a license by a notice in writing to execute any repairs in the licensed premises which are, in the opinion of such authority, necessary for the safety of the premises, the holder of the license shall execute the repairs within such period as may be specified in the notice.

9. Every vessel before being repaired or exhumed shall be made free of compressed gas and thoroughly cleaned. When a vessel is opened for cleaning or repairs, no lamp of any description either ordinary or electric, electric cables or fans and no articles, appliances or equipment capable of igniting flammable, vapors shall be brought near the vessel.

10. No person shall cause to repair or repair either by the use of fire, welding, hot riveting or brazing any vessel used for the storage of flammable gas unless it has been thoroughly cleaned and gas-freed or otherwise prepared for safely carrying out such hot work and certified in writing, by a competent person, to have been so prepared. Where the vessel has been certified as gas-free, the certificate shall be preserved by the licensee for a period of not less than three months and produced to the Chief Inspector, on demand.

11. No person shall enter any vessel used for the storage of a toxic or corrosive gas unless he is adequately protected by means of clothing, gas masks and such other protective equipment.

12. Compressed gas shall enter the vessel through sound pipes having no leaks at any place.

13. The vessel shall not be filled between the hours of sunset and sunrise, except in such manner and under such other condition or conditions as are specifically endorsed on the license by the licensing authority.

14. No artificial light capable of igniting flammable vapors shall at any time be present within 9 meters of the vehicle and the loading or unloading points during the transfer of the compressed gas and no person engaged in such transfer shall smoke.

15. No compressed gas shall be removed from the vessel except by means of transfer facilities marked in the plan attached hereto.

16. All electrical equipment such as motors switches, starters, etc., used for transfer of flammable compressed gas shall be of flameproof construction conforming to approved specifications.

17. Every person managing or employed on or in connection with the licensed premises shall abstain from any act whatsoever which tends to cause fire or explosion and which is not reasonably necessary and to the best of his ability, shall prevent any other person from doing such act.

18. The licensee shall provided for each licensed premises a minimum of two portable foam types or dry chemical type fire extinguishers of 9 Kgs. capacity each, which shall be kept ready at convenient location for immediate use in the event of any fire.

19. Except for necessary pipes and valves and approved electric lights the space within the licensed premises shall be kept entirely clear and unoccupied.

20. All valves in the premises must be permanently marked in a manner clearly indicating the direction of opening and shutting the valve.

21. Any accident, fire or explosion within the licensed premises which is attended with loss of life or serious injury to person or property shall be immediately reported to the nearest Judicial Magistrate or to the officer in charge of the nearest police station and by telephone to the Chief Inspector of Explosives.

22. Free access to the licensed premises shall be given at all reasonable times to any of the Inspector of Explosives and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed.

(ii)	All metal pipes shall be flexible pipes shall be tested once every 6 months by a competent engineer holding license to ascertain fitness and compliance with the requirement of strength laid down above.

(iii)	(a) 	A complete and permanent record of such testing shall be maintained in the licensed premises.

(b) 	The date of the last test shall be recorded on the pipes and pipe sections concerned in a distinctive manner.

23.	The license shall not deliver from the licensed premises:-

(a)	Petroleum in bulk to any vessel used in the carriage of petroleum in bulk by 	water; and

(b)	Any petroleum in bulk shall be delivered to any vehicle used for the transport of 	petroleum in bulk by road unless such vehicle is licensed by the Chief Inspector.

FORM ‘Q’

[Article 12 of Schedule I ]

LICENSE TO TRANSPORT PETROLEUM PRODUCT IN BULK ON LAND BY MECHANICALLY PROPELLED VEHICLE

License No. ………………………………			Fee Rs. ……………...

License is hereby granted to …………………………………………to transport petroleum in bulk on land by the vehicle as described below subject to the provisions of the Petroleum Act, 1934, and the rules made there under and to the further conditions of this license.

This license shall remain valid up to the …………day of ……20……

Date of issue ……………………………………………

Licensing Authority

DESCRIPTION OF VEHICLE

(a)	Make and model		        ……………………………………

(b)	Engine number		        ……………………………………

(c)	Chassis number		        ……………………………………

(d)	Registration number		        ……………………………………

(e)	Name of the registered owner         ……………………………………

(f)        Name of carriage contractor            ……………………………………

(g)	Total number of compartments       ……………………………………

(h)	Capacity of each compartment        ……………………………………

(i)	Class(es) of petroleum authorized

to be carried in the vehicle               ……………………………………

This license is liable to be cancelled if the licensed premises when inspected are not found conforming to the description and conditions attached hereto and contravention any of the rules and conditions, under which this license is granted, is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

CONDITIONS OF LICENSE

      - The license or its authenticated copy shall at all times be kept in the licensed vehicle and produced on demand by an Inspection Officer.

2.	Only reasonable persons who are conversant with the conditions of this license shall be employed for driving the licensed vehicle or attending to it.

3.	The licensed vehicle shall be constantly attended to by a responsible person and by at least two persons while it is transporting petroleum;

Provided that the licensed vehicle, if its tanks and compartments are empty, be left un-attended in a place approved for the purpose, in writing by the Chief Inspector.

4.	The licensed vehicle shall at all times carry;

  - A portable fire-extinguisher of capacity not less than 9 liters and suitable for extinguishing oil fires; the extinguisher shall be kept unlocked at an easily accessible position which shall be away from the discharge faucets of the vehicle;

(b)	A separated oil-tight and electrically continuous hose with coupling to match the discharge faucet of the licensed vehicle and the inlet pipe into which the petroleum carried in the vehicle is to be unloaded; and

(c)	A flexible cable for electrical bonding; the cable shall be at least 5 meters long and shall have at each end a suitable clamp or clip.

5.	The licensed vehicle shall not be loaded or unloaded except in a place approved for the purpose, in writing, by the Chief Inspector.

Provided that the licensed vehicle may be unloaded at any other place with all due precautions and under adequate supervision if such unloading is necessitated due to an accident or breakdown.

  - Petroleum carried in the licensed vehicle shall not be directly transferred into any container or into the fuel tank of any motor conveyance or an internal combustion engine.

7.	The licensed vehicle shall not be loaded if any tank or compartment, pipe, valve emergency discharge control of any safety fitting become leaky, defective or otherwise insecure until necessary reapers have been carried out satisfactorily and in the event of any leak in the tanks or compartments, until the leak is thoroughly repaired and all the tanks or compartment’s are tested hydrostatically to a pressure of 0.316 kg/sq.cm. for a duration of not less than one hour and found satisfactory.

8.	Before petroleum is loaded into or unloaded from the licensed vehicle;

  - its engine shall be stopped and the battery shall be isolated by a proper switch or otherwise;

  - its wheel shall be secured by brakes or by scotching and in the case of animal drawn vehicles, animal shall be unhitched and removed;

  - A reasonable persons shall be in attendance and remain so until load or from which it is to be unloaded or loaded;

  - The correct filling or discharge hose shall be selected and connected by oil tight coupling at both ends; and

  - A reasonable person shall be in attendance and remain so until loading or unloading is over and the tanks and compartments have been sealed.

9.	Except when called upon by traffic signals or required by an Inspector of Explosives or a Sampling Officer, the licensed vehicle shall not stop on any road, congested area or a place, which is not, a place approved in writing under these rules for the loading, unloading or stabling of such vehicle.

    - No smoking and no fire or artificial light or any article capable igniting inflammable vapor shall be allowed on the licensed vehicle.

    - The licensed vehicle shall not be used for carrying passenger or any article other than petroleum.

    - The licensed vehicle shall not be allowed to be repaired welding, soldering, brazing or hot riveting until its tanks. Compartment’s pipe and valve have been thoroughly cleaned and examined by a competent person and certified by him in writing to be free from inflammable vapor or oil.

    - No alteration in the licensed vehicle or its safety fitting shall be carried out without the previous sanction in writing of the licensing authority. Such alteration so sanctioned shall be endorsed on this license by an amendment.

    - Every facility shall be given at all reasonable times to any Inspector or Sampling Officer for ascertaining that the rules and the conditions of this license are duly observed or for drawing samples.

    - Causing loss of human life or serious injury to person or property shall be immediately reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station and by telegraph/fax or telephone to the Chief Inspector of Explosives (Telegraphic address, “Explosives, Rawalpindi”).

FORM  ‘R’

[Article 13 of Schedule I ]

LICENCE TO TRANSPORT LIQUEFIED PETROLEUM GAS IN BULK ON LAND BY MECHANICALLY PROPELLED VEHICLE.

License No.____________________                                               Fee Rs.__________________

License is hereby granted to ___________________________________________ to

transport liquefied petroleum gas by the vehicle as described below subject to the provisions of the Petroleum Act 1934 the rules made there under and to the further conditions of this license.

This license will remain valid up to the 31st day of December ------------- (year)

Date of Issue:                                                                             Chief Inspector of Explosives

Approved Plan No.    ______________________       Dated      _________________________

DESCRIPTION OF THE VEHICLE

Make and Model ________________________ Engine Number ________________________

Chassis Number _______________________Registration Number _____________________

Name of the registered owner ____________________________________________________

Chemical name of the liquefied petroleum gas to be carried in the Vehicle ______________

Authorized carrying capacity of the container ______________________________________

ENDORSEMENT OF RENEWALS

| Date of Renewal | Date of Expiry | Signature and office Stamp of the Licensing Authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed vehicle is not found conforming to the description of approved plan by Department of Explosives No. ____________   dated _________   and conditions attached thereto, and contravention of any of the  rules and conditions under which this license is granted and the holder of this license is also punishable with fine which may extend to thirty thousand rupees.

CONDITIONS

1. 	The license or its authenticated copy shall at all times be kept in the licensed vehicle and produced on demand by an  Inspector.

2. 	Only responsible persons who are conversant with the conditions of this license shall be employed for driving the licensed vehicle or attending to it.

3. 	The licensed vehicle shall be constantly attended to by a responsible person and by at least two persons while it is transporting liquefied petroleum gas.

Provided that the licensed vehicle may, if empty, be kept unattended in a place approved for the purpose, in writing, by the Chief Inspector.

4. 	The licensed vehicle shall at all times carry –

(a)	at least two portable fire extinguishers of capacity not less than 9 liters and suitable for extinguishing chemical fire;

(b) 	a strong flexible cable for electrical bonding in case of vehicle used for 		transportation of  flammable liquefied petroleum gas; the cable shall be at least 5 		meters long and shall have at each end a suitable clamp or clip.

5. 	The licensed vehicle shall not be loaded or unloaded except in a place which is approved within the premises licensed for the purpose under the rules by the Chief Inspector.

6. 	No vehicle shall discharge any liquefied petroleum gas directly; into any process vessel in operation or vehicles fuel tank

7. 	The licensed vehicle shall not be loaded if any of the fitments including vessel becomes leaky, defective or otherwise insecure.

8. 	Before liquefied petroleum gas is loaded into or unloaded from the licensed vehicle –

(a) its engine shall be stopped and the battery shall be isolated by a proper switch or

otherwise;

(b) its wheels shall be secured by brakes or by scotching;

(c) its chassis shall be electrically bonded by a cable with the pipe into or from which it is to be loaded or unloaded, in case of vehicle used for transportation of flammable gas;

(d) the correct filling or discharge pipe connections are made at both ends;

(e) a responsible person shall be in attendance and remain so until loading or unloading is over and the vehicle has been sealed.

9. 	Except when called upon by traffic signals or required by the licensing authority or any other officer entrusted with the job of enforcing the rules, the licensed vehicle shall not stop on any road, congested area or a place which is not a place situated within the premises licensed under the rules for the loading and unloading of vehicle.

10. 	No smoking and no fire or artificial light or any article capable of igniting flammable vapors shall be allowed on the licensed vehicle used for the transportation of any flammable gas.

11. 	The licensed vehicle shall not be used for carrying passengers.

12. 	The licensed vehicle shall not be allowed to be repaired.

Provided that replacement by any of the fitments of the pressure vessel may be done without involving any hot work.

13. 	No alteration in the licensed vehicle or its safety fittings shall be carried out without previous sanction in writing of the licensing authority. Such alteration so sanctioned shall be endorsed on the license by an amendment.

14. 	Every facility shall be given at all reasonable times to any Inspector  for ascertaining that the rules and the conditions of this license are duly observed.

15. 	Any accident, fire or explosion occurring in the licensed vehicle, which is attended with loss of human life or serious injury to person or property shall be immediately reported to the nearest magistrate or to the officer in-charge of the nearest police station having jurisdiction and by telephone or by fax to the Chief Inspector of Explosives.

16.	Liquefied petroleum gas shall not pass through congested or/and busy city roads as far as possible.

17.	The maximum speed limit shall be restricted to 25KM/hrs.

18.	The word “DANGER” shall conspicuously be written on the back of the tanker in red color with signs of danger.

19. 	A red flag of adequate size shall be installed on the drivers cab.

20. 	A report about satisfactory performance to the tanker along with details of problems/difficulties faced in their operation, if any shall be furnished to this office on monthly basis.

FORM  ‘S’

[Article 14 of Schedule I ]

LICENSE TO TRANSPORT COMPRESSED NATURAL GAS IN BULK ON LAND BY MECHANICAL PROPELLED VEHICLE. (COMPRESSED NATURAL GAS

STORAGE CYLINDER MOUNTED IN VEHICLE FOR

FUELING ARE EXEMPTED).

License No.____________________                                               Fee Rs.__________________

License is hereby granted to ___________________________________________ to transport compressed natural gas   by the vehicle as described below subject to the provisions of the Petroleum Act 1934 the rules made there under and to the further conditions of this license.

This license will remain valid up to the 31st day of December_______(year)

Date of Issue:                                                                             Chief Inspector of Explosives

Approved Plan. No.    ________________________       Dated   ________________________

DESCRIPTION OF THE VEHICLE

Make and Model _______________________ Engine Number ________________________

Chassis Number ______________________Registration Number _____________________

Name of the registered owner ___________________________________________________

Chemical name of the compressed natural gas  to be carried in the Vehicle ______________

Authorized carrying capacity of the container ______________________________________

ENDORSEMENT OF RENEWALS

| Date of Renewal | Date of Expiry | Signature and office Stamp of the Licensing Authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed vehicle is not found conforming to the description of approved plan by Department of Explosives No. ____________   dated _________   and conditions attached thereto, and  contravention of any of the  rules and conditions under which this license is granted and the holder of this license is also punishable with fine which may extend to thirty thousand rupees.

CONDITIONS

1. 	The license or its authenticated copy shall at all times be kept in the licensed vehicle and produced on demand by an  Inspector.

2. 	Only responsible persons who are conversant with the conditions of this license shall be employed for driving the licensed vehicle or attending to it.

3. 	The licensed vehicle shall be constantly attended to by a responsible person and by at least two persons while it is transporting compressed natural gas.

Provided that the licensed vehicle may, if empty, be kept unattended in a place approved for the purpose, in writing, by the Chief Inspector.

4. 	The licensed vehicle shall at all times carry –

(a)	at least two portable fire extinguishers of capacity not less than 9 liters and 	suitable for extinguishing chemical fires;

(b) 	a strong flexible cable for electrical bonding in case of vehicle used for 	 transportation of  flammable compressed natural gas; the cable shall be at least 5 meters long and shall have at each end a suitable clamp or clip.

5. 	The licensed vehicle shall not be loaded or unloaded except in a place which is approved within the premises licensed for the purpose under the rules by the Chief Inspector.

6. 	No vehicle shall discharge any compressed natural gas directly, into any process vessel in operation or vehicles fuel tank.

7. 	The licensed vehicle shall not be loaded if any of the fitments including vessel becomes leaky, defective or otherwise insecure.

8. 	Before compressed natural gas is loaded into or unloaded from the licensed vehicle –

(a) its engine shall be stopped and the battery shall be isolated by a proper switch or

otherwise;

(b) its wheels shall be secured by brakes or by scotching;

(c) its chassis shall be electrically bonded by a cable with the pipe into or from which it is   to be loaded or unloaded, in case of vehicle used for transportation of flammable gas;

(d) the correct filling or discharge pipe connections are made at both ends;

(e) a responsible person shall be in attendance and remain so until loading or unloading is over and the vehicle has been sealed.

9. 	Except when called upon by traffic signals or required by the licensing authority or any other officer entrusted with the job of enforcing the rules, the licensed vehicle shall not stop on any road, congested area or a place which is not a place situated within the premises licensed under the rules for the loading and unloading of vehicle.

10. 	No smoking and no fire or artificial light or any article capable of igniting flammable vapors shall be allowed on the licensed vehicle used for the transportation of any flammable gas.

11. 	The licensed vehicle shall not be used for carrying passengers.

12. 	The licensed vehicle shall not be allowed to be repaired.

Provided that replacement by any of the fitments of the pressure vessel may be done without involving any hot work.

13. 	No alteration in the licensed vehicle or its safety fittings shall be carried out without previous sanction in writing of the licensing authority. Such alteration so sanctioned shall be endorsed on the license by an amendment.

14. 	Every facility shall be given at all reasonable times to any Inspector  for ascertaining that the rules and the conditions of this license are duly observed.

15. 	Any accident, fire or explosion occurring in the licensed vehicle, which is attended with loss of human life or serious injury to person or property shall be immediately reported to the nearest magistrate or to the officer-in-charge of the nearest police station having jurisdiction and by telephone or by fax to the Chief Inspector of Explosives.

16.	Compressed natural gas shall not pass through congested or/and busy city roads as far as possible.

17.	The maximum speed limit shall be restricted to 25KM/hrs.

18.	The word “DANGER” shall conspicuously be written on the back of the tanker in red color with signs of danger.

19. 	A red flag of adequate size shall be installed on the drivers cab.

20. 	A report about satisfactory performance to the tanker along with details of problems/difficulties faced in their operation, if any shall be furnished to this office on monthly basis”; and

(21)	after Schedule-III, the following new Schedule shall be added, namely:-

“SCHEDULE-IV

[See rule 98 A]

- Shops may be allowed where petrol pumps, compressed natural gas stations and Liquefied Petroleum Gas Automotives fuel stations are located on highways and main roads.

- The dimensions of plot for petrol pump, compressed natural gas station, liquefied petroleum gas, Automotive fuel station for shop shall meet the all safety distance requirements and isolation distances as mentioned in the relevant rules and regulations.

- Shop shall be at least 10 meters away from petroleum storage tanks or Liquefied gas storage tanks gas kits and all dispensing units.

- All other ancillary facilities other than shop shall be at least 5 meter away from petroleum storage tanks or liquefied gas storage tanks, gas kits and all dispensing units.

- Area of shop shall not be more than 15% of total covered area excluding canopy at the petrol pump premises, liquefied petroleum gas fuel stations, compressed natural gas stations. A separate fee of rupees thirty per square feet shall be charged for any additional area of shop.

- Entrance to shop shall be kept clear at all times.

- There shall be no opening from adjacent premises to a shop.

- Shop shall not be opened at any petrol pump, compressed natural gas station, liquefied petroleum gas, Automotive fuel station without prior approval in writing of the Chief Inspector of Explosives.

- Roof of the shop shall not be used for any other purpose.

- Heaters, burners or any appliance likely to cause spark shall not be used in site a shop, however a micro-wave oven may be used.

- Seating arrangement for customers shall not be provided inside a shop.

- Only packed food items, cold drinks, souvenirs and medicines shall be stored.

In case of other items permission of the Chief Inspector shall be obtained in 	writing.

- At least two fire extinguishers of 10 Kg. each shall be provided exclusively for shop.

- A separate fee per year or part thereof shall be paid for every ancillary facility, as specified below, which is not directly connected with the storage and distribution of petroleum, compressed natural gas, liquefied petroleum gas through dispensers.

Ancillary Facility

1.	Fee for shop						15,000/-

2.	Fee for kit conversion shop				10,000/-

3.	Fee for vehicle wash/service station			10,000/-

4.	Fee for tyre puncture shop				5,000/-

5. 	Fee for Lube or service station			5,000/-

6.	Fee for Public Call Office, Fax, ATM Facilities.	5,000/-”

[F.No.                  ]

(                              )