THE PETROLEUM RULE, 1937

Previously published under the Government of India (Department of Industries & Labour) Notification No. M-826 (6), dated 23-3-1937:-

In exercise of the powers conferred by section 4, sub-section (2) of section 5, sub-section (2) of section 14, sections 21 and 22 and sub-section (1) of section 29 of the Petroleum Act, 1934 (XXX of 1934), read with section 22 of the General Clauses Act, 1897 (X of 1897), the Governor General in Council is pleased to make the following rules which have been Previously published as required by sub-section (2) of section 29 of the first-mentioned Act, namely :-

RULES

CHAPTER I

PRELIMINARY

1.	Short title and application. – These rules may be called the Petroleum Rules, 1937.

2.	Supersession and savings. – (1) All notification and rules issued, and all appointments made by local Governments under the Petroleum Act, 1899, and all rules made by the Governor General in Council under section 8 of that Act are hereby superseded, but -

- all licenses or duplicates granted or renewed and all fees imposed or levied shall be deemed to have been respectively granted, renewed, imposed or levied under the these rules; and

(ii)	all approval given and all powers conferred by or under any notification or rule so superseded shall, so far as they are consistent with the Act and these rules, be deemed to have been given or conferred by or under these rules.

2.	Anything not in conformity with these rules which was permitted to be done by or under any rule in force immediately before the coming into force of these rules, and which under these rules, may be permitted by the Chief Inspector to be done, shall be deemed to have been so permitted by the Chief Inspector, unless the Chief Inspector, after such notice of his intention as he considers reasonable, declares that it is not so permitted.

3.	Definitions. –       In these 	rules, unless there is anything repugnant in the subject or context, -

- “The Act” means the Petroleum Act, 1934 ;

- “Chief Inspector” means the Chief Inspector of Explosives in Pakistan ;

- “Conservator of the Port” includes any person acting under the authority of the officer or body of persons appointed to be Conservator of Port under section 7 of the Ports Act, 1908 ;

- “District Authority” means – the District Nazim and the City Nazim;

- “Heavy Petroleum” means petroleum which has its flashing-point not below 130 degrees F;

- “Inspector” means an officer authorized by the Central Government under sub-section (1) of section 13 of the Act ;

Notes and References.    – The following officers have been authorized in the areas specified by Notification No. M-826(1), dated the 22nd March 1937 as amended by Notification No. M-826(4), dated the 15th September 1937 as amended in Pakistan.

Officers					Areas

1.	The Chief Inspector, Inspector and Assistant	              All provinces and Capital of the

Inspector of Explosives					Federation including Baluchistan

2.	All District Magistrates.					Their respective Districts.

3.	All Magistrates subordinate to the District		Their respective jurisdiction.

Magistrate.

4.	All Police officers of rank not below that of 	              The respective areas over which their

Inspector							authority extends.

- “Installation” means any premises within which any place has been specially prepared for the storage of petroleum in bulk, but does not include a well-head tank ;

- “Petroleum in bulk” means petroleum contained in a receptacle exceeding two hundred gallons in capacity ;

- “Protected works” means buildings or places in which persons dwell or assemble or where any combustible material is stored and includes docks, wharves, public roads and streets, public foot-paths and public parks, but do not include any building or place which forms part of an installation. [Vide, Ministry of Industries Notification No. S.R.O. 3 B (K)/61, dated 15th February, 1961, published in Gazette of Pakistan, dated 3rd March 1961, Page 119.]

(j)	“Sampling Officer” means an officer authorized by the Central Government. under sub-section (1) of Section 14 of the Act.

Notes and References. – Sampling officers were appointed by Notification No. M-826(2), dated the 22nd March 1937 [amended by Notification No. M-826 and 826(5), date the 26th August, 1937 and 15th September 1937 respectively] as amended in Pakistan.

Officers					Areas

1.	The Chief Inspector, Inspector and Assistant	              All provinces and Capital of the

Inspector of Explosives					Federation including Baluchistan

2.	All District Magistrates.					Their respective Districts.

3.	All Magistrates subordinate to the District		Their respective jurisdiction.

Magistrate.

4.	All Police officers of rank not below that of 	              The respective areas over which their

Inspector							authority extends.

5.	Preventive Officers, Custom House			The Port of Karachi

Karachi

6.	Preventive Officers, Custom House			The Port of Chittagong

Chittagong.

- “Storage shed” means a building used for the storage of petroleum otherwise than in bulk, whether it forms or does not form part of an installation, but does not include a building used for the storage of petroleum exempt from license under section 7, 9 or 9 of the Act ;

- “Testing officer” means an officer authorized by the Central Government to test petroleum under section 17 of the Act ; and

Note and References. – The following officers have been authorized to test petroleum and to grant certificates of the result of such test by Notification No. M-826, dated the 17th March 1937, as amended by Notification No. M-826 (6) dated the 15th September 1937, NO. M-826, dated the 20th October 1937 and No. M-826, dated the 10th May 1939 as amended in Pakistan:

1.	The Chief Inspector, Inspector & Assistant Inspector of Explosives.

- The Civil Surgeon, Chittagong.

- The Chemical Examiner, Custom House, Karachi.

- The Special Chemical Adviser to the Central Board of Revenue, Lahore.

- “Well-head tank” means tank into which crude petroleum flowing or being pumped from a well is first discharged;

- “District Coordination Officer” means an officer appointed in a District who shall be a civil servant of the Federation or of a Province; and

- “Magistrate” means a Judicial Magistrate and includes a Special Judicial Magistrate.

4.	Excluded petroleum. – Nothing in these rules, except Chapter IX, applied to petroleum, which has its flashing-point not below 200 degrees F.

CHAPTER II

Importation of Petroleum

PART I

GENERAL

5.	License for import of dangerous petroleum. Save as provided in section 8, 9 and 10 of the Act, dangerous petroleum shall no be imported except under a license granted under these rule.

6.	Petroleum exempted. – (1) Nothing in this Chapter applies to –

(a)	dangerous petroleum, not exceeding 6 gallons in quantity which is not intended for sale ;

- dangerous petroleum contained in any fuel tank incorporated in a motor conveyance ;

- non-dangerous petroleum, comprised in a ship’s stores and manifested as such, provided it is not of an unreasonably large amount.

(2)	If any question arises as to whether any petroleum manifested as ship's stores is of an unreasonably large amount, the decision thereon of the Collector of Customs shall be final.

(3)	Nothing in rules 5 and 13 shall apply to petroleum imported by Armed Forces of Pakistan.

PART II

IMPORTATION BY SEA

7.	Importation by sea. – Petroleum shall not be imported by sea except into the ports of Karachi.

8.	Declaration by master of ship carrying petroleum or by the ship’s agent. – The master of every ship carrying petroleum shall deliver to the pilot before entering any of the ports mentioned in rule 7, a written declaration in Form A under his signature ;

Provided that if, in anticipation of a ship’s arrival, the agent for such ship delivers to the Conservator of the Port a written declaration as aforesaid under his signature, no such declaration need be made by the master of the ship.

9.	Delivery of certificate. – If the master or agent declares that nay petroleum which it is intended to land at that port or at any other port in Pakistan is petroleum certified in accordance with rule 11 he shall deliver to the pilot or Conservator of the Port, as they case may be along with his declaration, the certificate relating to such petroleum.

10.	Declaration and certificate to be forwarded to Collector of Customs. – Every declaration and certificate delivered to a pilot under rules 8 and 9 shall be made over by him without delay to the Conservator of the Port, and every declaration and certificate received by the Conservator of the Port under rule 8 or rule 9 or this rule shall be forwarded by him, with all convenient dispatch, to the Collector of Customs of the port.

11.	Certified petroleum. – For the purposes of rules 9 and 156 Form A, petroleum shall be deemed to be certified if it is accompanied by a certificate in Form B granted at the port of shipment or, subject to the approval of the Collector of Customs, in any other form containing the material particulars required by Form B, and has a flashing point not below 76 degrees F;

Provided that the Collector of Customs may refuse to accept any certificate, if he is not satisfied as to its genuineness.

12.	Anchorage of ships carrying petroleum. – Every ship having petroleum on board shall be anchored at such anchorage as the Conservator of the Port shall appoint in this behalf and shall not leave such anchorage without the general or special order of the Conservator of the Port subject to such condition as may be specified in such order. Such anchorage shall in no case be the same as that for vessels laden with explosives and shall be at such distance from the anchorage for vessels laden with explosives as to render it impossible for a fire originating at the former anchorage to affect vessels anchored at the latter.

13.	Production of certificate and license for import. – (1) Every person desiring to import petroleum shall furnish personally or through his agent to the Collector of Customs a certificate of storage accommodation in Form C signed by the said person or his agent ;

Provided that, where the importer intends to import both dangerous and non-dangerous petroleum, separate Forms shall be furnished for dangerous and non-dangerous petroleum.

Provided further that this sub-rule shall not apply where the quantity of non-dangerous petroleum to be imported by any one consignee does not exceed 500 gallons, or where the quantity of dangerous petroleum to be imported does not exceed 60 gallons.

(2)	Every person desiring to import dangerous petroleum shall produce, personally or through his agent, before the Collector of Customs his license for the import and storage of such petroleum.

14.	Permission of Collector of Customs to land petroleum. – (1) No imported petroleum shall be landed except with the permission of the Collector of Customs.

- If the Collector of Customs, after receiving –

- the testing officer’s report on any petroleum or, in the case of petroleum of Burmese origin a certificate containing the particulars required by Form B granted by a testing officer appointed by the Government of Burma ;

- the certificate required by sub-rule (1) of rule 13 ; and

- the license, if require by sub-rule (2) of rule 13 ;

and after making such further inquiries as he deems necessary, is satisfied that the petroleum can lawfully be imported and that there is suitable accommodation for it, he shall permit it to be landed.

(3)	If the Collector of Customs is satisfied that any petroleum imported otherwise than in bulk is not intended to be stored in Pakistan, but is intended to be dispatched immediately after landing to a territory which is not part of Pakistan, he may waive the requirements of rule 5 and 13 and by written order permit, subject to such conditions as he may specify, such petroleum to be landed for the purpose of immediate dispatch to the territory in question.

(4)	Nothing in this rule shall affect the power of the Collector of Customs to detain the petroleum under any other law or rule for the time being in force.

15.	Landing of non-dangerous petroleum in anticipation of the testing officer’s report. – (1) Notwithstanding anything contained in rule 14, where the consignee furnishes a guarantee to re-ship the petroleum if the testing officer’s report proves unfavourable, the Collector of Customs may, in anticipation of the testing officer’s report, permit any petroleum which he believes to be non-dangerous to be discharged into boats or to be landed.

(2)	The permission granted under sub-rule (1) shall be subject to the condition that the boats into which the petroleum is discharged, shall remain at such place as the Conservator of the Port may appoint or that the petroleum shall be landed at a landing-place duly appointed for this purpose by him and stored in an installation under these rules.

16.	Unloading of petroleum in bulk. – Subject to the rules in Part II of Chapter III, petroleum imported in bulk shall be discharged into storage tanks on shore either directly or by means of barges or lighters specially constructed for carrying petroleum in bulk and only at such places as the Conservator of the Port may by general or special order direct.

17.	Unloading of petroleum otherwise than in bulk. – (1) Subject to the rules in Part II of Chapter III, petroleum imported otherwise than in bulk shall be landed either at jetties provided for the purpose, or in barges or lighters and only at such places as the Conservator of the Port shall direct.

(2)	No petroleum contained in casks, drums or other receptacles shall be landed unless such receptacles are free from leakage and of such strength and construction as not to be liable to be broken or to leak except in case of gross carelessness or extraordinary accident.

Provided that petroleum contained in casks, drums or other receptacles which do not satisfy the requirement of this sub-rule may, subject to the rules in part II of Chapter III and to such conditions as the Conservator of the Port may impose, be landed at a separate landing place approved for the purpose.

18.	Transshipment of petroleum. – Petroleum may be transshipped from one to another for conveyance to any other port, whether within or beyond the limits of Pakistan, subject to the rules in Part II of Chapter III.

19.	Heavy petroleum. – (1) Nothing in rules 12 to 18 inclusive applies to heavy petroleum.

(2)	Notwithstanding anything contained in the preceding rules, if the master of, or agent for, a ship produces a certificate that any petroleum on board is heavy petroleum, the Collector of Customs shall allow it to be discharged in the same manner as ordinary cargo. ;

Provided that the sampling officer may at any time require a sample of any of the petroleum to be delivered to him, with a view to having it tested.

PART III

IMPORTATION BY LAND

20.	Importation by land. – Petroleum shall not be imported by land except at points to be specified by the Central Government in this behalf and unless:-

- it is accompanied by a declaration from the consignor regarding the nature and the quantity of the petroleum

- the importer holds such storage license as may be required under these rules;

- the receptacles in which petroleum is imported conform to rule 27 of Rules; and

- Pakistan Customs Regulations in force for the time being are complied with.

21.	Permission of Collector of Customs to release Petroleum imported by land.

  - No petroleum imported by land shall be landed except with the permission of the Collector of Customs.

  - If the Collector of Customs, after receiving.

- the Testing Officer’s report on any petroleum in Form ‘G’

- the certificate of Storage accommodation in form ‘C’ signed by the consignee or his agent.

- the license as may be required under these Rules, and after making such further enquiries as he deems necessary, is satisfied that the Petroleum can lawfully be imported and that there is suitable accommodation for it he shall permit it to be land.

22.	Omitted.

23.	Omitted.

CHAPTER III

Transport of Petroleum

PART I

GENERAL

24.	Prevention of accidents. – All due precautions shall be taken at all times to prevent accident by fire or explosions.

25.	Prevention of escape of petroleum. – All due precautions shall be taken at all times to prevent any escape of petroleum during transport especially into any drain, sewer, harbor, river or watercourse.

26.	Empty receptacles. – All empty tanks or other receptacles which have contained dangerous petroleum or which have contained non-dangerous petroleum in bulk shall, except when they are opened for the purpose of cleaning them and rendering them free from petroleum vapor, be kept securely closed unless they have been thoroughly cleaned and freed from petroleum vapor.

27.	Receptacles for dangerous petroleum. – (1) Dangerous petroleum, if not in bulk, shall be contained in gas-tight tinned, galvanized or otherwise externally rust-proofed sheet iron or steel receptacles which shall be fitted with well-made filling aperture and well-fitting screw plugs, or with screw caps or other caps with metal air-tight under-caps. The receptacles shall be kept in proper repair.

(2)	No receptacles, other than tanks on tank-carts of a type approved in writing by the Chief Inspector, shall be of more than 65 galls capacity excluding the air-space prescribed by sub-rule (7).

(3)	The receptacles, other than tanks on tank-carts, shall be of a type approved in writing by the Chief Inspector and shall have the following thickness of metal:-

Not less than

not exceeding 2 gallons		…	…	…	…	…	27 B. G.

exceeding 2 but not exceeding 4 gallons	…	…	…	22 B. G.

exceeding 4 but not exceeding 30 gallons	…	…	…	18 B. G.

exceeding 30 but not exceeding 45 gallons	…	…	…	17 B. G.

exceeding 45 gallons	…	…	…	…	…	…	16 B. G.

Provided that the Chief Inspector may, by written order, permit the use in any particular case of receptacles having thickness of metal less than that specified in this sub-rule.

(4)	Where the approval of the Chief Inspector is sought to a type of receptacle not previously approved, three copies of a detailed drawing thereof to scale be forwarded to him.

(5)	The receptacles shall be so constructed and secured as not to be liable, except under circumstances of gross negligence or extraordinary accident to become defective, leaky or insecure in transit.

(6)	The receptacles shall bear a stamped, embossed, painted or printed warning exhibiting in conspicuous character the words “Petrol” or “Motor Spirit” or an equivalent warning of the dangerous nature of the petroleum.

(7)	An air-space of not less than 5 per cent, of its capacity shall be left in each tank, drum or other receptacles containing dangerous petroleum.

(8)	Nothing in sub-rules (1), (2), (3), (4) and (6) shall apply to receptacles in the possession of Armed Forces of Pakistan.

28.	Receptacles for non-dangerous petroleum. – (1) Non-dangerous petroleum, if not in bulk, shall be packed in air-tight tins or drums, of steel or iron or in other receptacles not easily broken or in tanks permanently fixed to carts, wagons, boats or other means of carriage, and of types approved by the Chief Inspector.

(2)	An air-space of not less than 5% of its capacity shall be left in each tank, drum or receptacle contained non-dangerous petroleum of a flash point below 150 degrees F.

Provided that, in the case of an un-berthed passenger ship to which Part IV of the Merchant Shipping Act, 1923 applied the petroleum shall be packed either in tins enclosed in outer wooden cases or in hermetically sealed iron or steel drums or, alternatively in the case of heavy petroleum, in sound well-coopered wooden casks of not more than 50 gallons capacity.

29.	Restriction on delivery and dispatch of petroleum. – (1) No person shall delivery any petroleum to any one [in Pakistan] other than the holder of a storage license or his authorized agent or a Port Authority or railway administration.

(2)	No person shall dispatch any petroleum to any one in Pakistan other than holder of a storage license.

(3)	Notwithstanding anything contained in sub-rule (2), non-dangerous petroleum not exceeding 3,000 gallons in quantity packed in sealed air-tight tins or drums of steel or iron may be dispatched to a person not holding a storage license, provided that the person dispatching the petroleum has satisfied himself that prior arrangements have been made by the person to whom the petroleum is dispatched for the immediate disposal in the original packages of any quantity in excess of 500 gallons.

(4)	This rule shall not apply to the delivery or dispatch of petroleum in quantities which are permitted by the Act or these rules to be stored without license, or to any petroleum in the possession of the Armed Forces of Pakistan.

PART II

TRANSPORT BY WATER

30.	Conditions of carriage of petroleum in bulk by water. – (1) Petroleum in bulk shall not be carried by water except in ship or other vessel licensed annually for the carriage of petroleum in bulk by an officer appointed by the Central Government in this behalf, and the petroleum shall be stored in such part of the ship or other vessel and in such manner as may be approved by general or special order by the officer so appointed after consultation with the Chief Inspector:

Provided that -

- nothing in this rule shall apply to ships importing petroleum.

- Petroleum in tank-wagons may, with the permission in writing of the Chief Inspector and subject to such conditions as he may specify, be transported across a river by a recognized wagon ferry.

(2)	*The license referred to in sub-rule (1) shall be granted in such form and on payment of such fees as may be specified by the Central Government in this behalf and the license shall remain in force for a period of 12 months.

Notes and References. – Notification NO. M-826(2), dated the 22nd December 1938 prescribed the appended Form for the grant of licenses in respect of ship or other vessels for the carriage of petroleum in bulk by water and directs that fees on the following scale be payable for such licenses :-

Rs.

(a) 	ship or other vessel not exceeding 100 tons gross tonnage 		              500

(b)	for every additional 50 tons gross tonnage or fraction thereof	100

License for the carriage of petroleum in bulk by water.

Name of Vessel ………………………………………………………………………

Official No.       ………………………………………………………………………

Gross tonnage    ………………………………………………………………………

Name of owners………………………………………………………………………

The above vessel is hereby licensed for the carriage of petroleum in bulk by water, under the rule 30 of the Petroleum Rules, 1937, subject to the provision of these rules and the Petroleum Act, 1934.

The petroleum shall be stored only in –

- the following parts ** of the vessels –

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

*Inserted by Notification No. M-826(1), dated the 22nd December 1938

**The parts of the vessel and the manner of storage to be specified in detail by the licensing authority in consultation with the Chief Inspector of Explosives.

(2) the following manner, that is to say,

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------

This license shall remain in force till the 	day*** (twelve months from the date of issue of the license) 		of 196

Issued at 			the		day of 			196

Licensing authority appointed under

Rule 30 of the Petroleum Rules, 1937).

Notes and References. – This rule means, in effect, that petroleum may not be carried in a ship or other vessel in any receptacle exceeding two hundred gallons in capacity unless the vessel has been specially licensed for the purpose less than a year before, Notification No. M-826 (2), dated the 31st March 1937 as amended in Pakistan appoints the officers specified in the annexed Schedule as the officers to license under this rule ships or other vessel for the carriage of petroleum in bulk by water.

THE SCHEDULE

1.	The Principal Officer, Mercantile Marine Department, Karachi.

2.	The Engineer and Ship Surveyor, Narayanganj.

31.	Requirements as to construction of vessels. – Every ship or other vessel carrying petroleum in bulk, other than a recognized wagon ferry permitted to transport tank-wagons under proviso (b) to rule 30, must be of steel or iron well and substantially constructed with scantling of ample dimension in proportion to the size of the vessel.

32.	Tank fittings on vessels. – In petroleum tank-ships or other vessels used for the transport of petroleum other than heavy petroleum the following provisions shall apply:-

- all tanks shall be fitted with independent approved filling and suction pipes and valves or with stand-pipes with blank flanges, all pipes being carried down nearly to the bottom of the tanks, and no petroleum in bulk shall be taken on board or discharged except through such pipes and valves, unless otherwise permitted by the Chief Inspector in writing ;

- all tanks shall be fitted with manholes having screw down covers with petroleum-tight joints and, in the case of tanks intended for use with dangerous petroleum, with ventilators or relief valves of approved pattern properly protected with wire gauge of a mesh of not less than 28 to the linear inch ; and

- ventilators similarly protected shall be fitted to all spaces around tanks

Provided that the Chief Inspector may, by order in writing, exempt from the provisions of this rule any vessel which was employed in transporting petroleum in bulk before the 1st April 1937.

33.	Self-propelled barges. – The following conditions shall be observed in self-propelled barges transporting petroleum other than heavy petroleum:-

- the whole of the machinery shall be at the stern of the barge and shall be entirely separated from the cargo by a cofferdam consisting of two transverse petroleum-proof bulk-heads separated by a space of at least two feet six inches ;

- the barge shall be provided with a heavy wood belting; and

- suitable ventilators shall be fitted to the cargo  space ;

Provided that condition (a) shall not be applicable to any barge which was employed in transporting petroleum before the 1st April 1937.

34.	Petroleum in bulk on barges or flats. – (1) Petroleum in bulk shall not be transported in a barge or flat unless the barge of flat:-

- is self-propelled and carries at least four fire extinguishers, or

- is in tow or, or otherwise attended by, a steamer or tug carrying at least four fire extinguishers.

(2)	The fire extinguishers referred to in sub-rule (1) shall be of a pattern approved by the officer appointed under rule 30 and shall be fitted in position approved by him.

35.	Inflammable cargo, or passengers. – (1) No ship or other vessel shall carry petroleum in bulk if it is carrying passengers, or any inflammable cargo other than petroleum or coal.

(2)	This rule shall no apply to heavy petroleum used as fuel and carried in cellular double bottoms under engine and boiler compartments and under ordinary holds, and in peak tank, deep tanks or bunkers of approved construction; such oil fuel storage tanks and installation connected therewith shall comply with the provisions of rules 228 to 243 of the Merchant Shipping (Construction and Survey of Passenger Steamers), Rule, 1935.

35A. – Petroleum carried as cargo in un-berthed passenger ships. – Dangerous petroleum shall not be transported as cargo by an un-berthed passenger ship as defined in the Merchant Shipping Act, 1923 (XXI of 1923):

Provided that the certifying officer referred to in section 157 of the Merchant Shipping Act, 1923 (XXI of 1923), may, in cases where he is satisfied that no other means of transporting the petroleum are available, permit dangerous petroleum in quantity not exceeding 250 gallons to be transported otherwise than in bulk by an un-berthed passenger ship other than a country craft subject to –

- the condition that no more persons shall be carried in the ship than can with safety be accommodated in the ship’s life-boats in case of accident; and

- such other conditions as the certifying officer may, after consultation with the Chief Inspector, impose ;

Provided further that clause (a) of the foregoing proviso shall not apply in the case of un-berthed passenger ships engaged on voyages between ports situated in Pakistan or between any port or place on the Dominion of Pakistan in the course of which they do not go more than 20 miles from land.

35B. Transport by country craft. – No country craft shall carry dangerous petroleum if it is carrying passengers.

36.	Restrictions as to inflammable cargo. – (1) No steamer or tug employed in towing or otherwise attending a barge, flat or lighter carrying petroleum, other than heavy petroleum in bulk shall at the same time tow or otherwise attend any other vessel carrying an inflammable cargo other than petroleum or coal.

(2)	No such steamer or tug shall carry any inflammable cargo other than petroleum or coal.

(3) All such steamers or tugs shall be fitted with efficient spark arresters.

37.	Ventilation and cleaning of holds and tanks. – (1) Before any petroleum is discharged from a ship or vessel the holds of such vessel shall be thoroughly ventilated:

Provided that nothing in this sub-rule shall apply to any vessel carrying dangerous petroleum not exceeding 6 gallons or non-dangerous petroleum not exceeding 500 or heavy petroleum not in bulk.

(2)	After all petroleum has been discharged from any such vessel the holds, tanks and bilges of the vessel shall be rendered free from inflammable vapour.

(3)	Sub-rule (2) shall not apply to the tanks of a ship importing petroleum which leaves the port without delay after the discharge of cargo or remains only for the purpose of taking on board bunkers stores or ballast or for such other purposes as may be approved the Conservator of the Port, if the tanks of every such ship are securely fastened down immediately after the discharge of the cargo.

(4)	Sub-rule (2) shall not apply to barges or lighters continuously engaged in the transport of petroleum in bulk, if –

- an interval of not more than 72 hours is likely to elapse between an operation of unloading or discharging and the next loading operations; and

- the tanks are securely fastened down immediately after unloading.

(5)	Sub-rule (2) shall not apply to specially constructed steel tank motor-vessel approved by the Chief Inspector which are engaged in transport of petroleum in bulk on such rivers and on such parts thereof as may be approved by him in areas outside port limits, or by the Conservator of the Port within port limits, if the tanks of such vessels are securely fastened down immediately after unloading and the vessels depart not later than 12 hours after completion of discharge for their next place of loading.

(6)	All ships or other vessels which by sub-rules (3), (4) or (5) are exempted from the application of sub-rule (2) shall, until their holds and tanks have been rendered free from inflammable vapour comply with all the rules applicable to ship, or other vessels when carrying petroleum in bulk.

38.	Master of vessel especially responsible. – (1) The master or other officer in charge of any ship with petroleum on board or of any vessel certified under rule 30 shall be responsible that –

- all due precautions are taken for the prevention of accident in the loading or discharge of petroleum.

- so long as there is petroleum or inflammable vapour in a tank, all openings from the tank to the atmosphere, except the gas escape line, are kept closed and locked or otherwise fastened in a manner certified as satisfactory by the officer appointed under rule 30 ; and when it is necessary to take dips or samples, the ullage plugs or sighting ports are closed immediately this has been done ;

Provided that, subject to the provisions of clause (c), such master or officer in charge may cause the necessary openings to be opened or unlocked for the purpose of tanking on board or discharging non-dangerous petroleum, for cleaning the tanks, or for other sufficient reason.

- every person entering a tank wears a safety helmet of a description approved by the Chief Inspector, unless a Conservator of the Port or other officer appointed by the Central Government in this behalf has on payment of the fee prescribed in sub-rule (2) examined the tank with the air of a vapour-testing instrument and has certified it to be free from dangerous vapour ;

- the vessels and any steamer or tug towing or otherwise attending on such vessel exhibits conspicuously :-

  - from sunrise to sunset a red flag not less than three feet square with a whiter circular center six inches in diameter, if dangerous petroleum is carried, and a red flag not less than three feet square if non-dangerous petroleum is carried ; and

  - from sunset to sunrise such warning lights as may be required by the Conservator of the port ;

- the vessel, when carrying petroleum in bulk, at all times lies afloat unless otherwise permitted by general or special order in writing of the Chief Inspector or the Conservator of the Port ;

- the vessel, when carrying petroleum in bulk, is constantly under the control and personal supervision of a responsible person ;

- iron or steel hammers or other instruments capable of causing a spark are not used for the purpose of opening or closing the hatches or tank covers ; and

- footwear, which exposes any iron or steel, is not worn on the deck of any vessel while the loading or unloading of dangerous petroleum is proceeding.

(2)	A fee of one hundred rupees shall be payable by the Master or other Officer in charge of the ship or vessel for each test carried out under clause (c) of Sub-rule (1).

39.	Loading and unloading by night. – (1) Where adequate electric lighting is installed and rule 105 is complied with tank-ships and barges may discharge or load non-dangerous petroleum at any time and tank-ships and barges which have commenced the discharge into storage tanks on shore, or loading into their own tanks, of dangerous Petroleum in bulk before sunset may continue the said discharge or loading.

(2)	Should anything occur during discharging or loading dangerous petroleum after sunset which necessitates a repair or disconnection of the plan pipes or connections, such discharging or loading shall be discontinued until after sunrise.

(3)	Save as provided by sub-rule (1), petroleum shall not be discharged or loaded or landed between the hours of sunset and sunrise.

(4) 	This rule shall not apply to the refueling or aircraft by vessels certified under rule 30, subject to any conditions which the Chief Inspector may impose in this behalf.

40.	Loading and discharge of bulk petroleum. – (1) The loading and discharge of petroleum in bulk shall be by armored hose and metal pipes.

(2)	All pipes and other appliances used in the landing or loading of petroleum in bulk shall be free from leakage.

(3)	When a ship has finished discharging petroleum other than heavy petroleum, the pipe line shall be immediately emptied of petroleum by pumping water through the line.

(4)	The Chief Inspector may, by written order, grant exemption in any particular case from the provisions of sub-rules (1) and (3).

41.	Precautions on suspension of loading or discharge. – When the loading or landing of petroleum has been commenced such loading or landing shall proceed with due diligence, and, if it is discontinued, the tanks and holds of the ships or other vessels concerned and all loading or discharge valves shall be closed immediately.

42.	Naked lights, fire and smoking on board a vessel prohibited.  – No fire, naked light, fuses, matches, or other appliance for producing ignition or explosion and no smoking shall be allowed on board any barge, flat or lighter carrying petroleum in bulk, or on board any such vessel used for the transport of dangerous petroleum otherwise than in bulk or for the transshipment of petroleum to or from any vessel within the limits of any port :

Provided that nothing in this rule shall prevent the use on a self-propelled barge of the machinery of propulsion.

43.	Smoking, fire and lights prohibited during loading and unloading. – At all times during the loading or unloading of a ship or other vessel until such time as all petroleum shall have been loaded into or removed from the holds or tanks and the holds or tanks shall have been securely closed down and, in the case of landing, rendered free from inflammable vapour, there shall be no fire or artificial light or smoking on board such ship or other vessel or within 100 feet of the place where the petroleum is being loaded or landed;

Provided that this rule shall not apply to the use of lamps, cookers or other similar apparatus electric or otherwise, so designed, constructed and maintained as to be incapable of igniting inflammable vapour or, in the case of heavy petroleum, the cause of galley fires.

Provided further that this rule shall not apply to the discharging or loading of a ship, under conditions approved by the Conservator of the Port, by means of steam from her own boilers or power generated by electric motors or internal combustion engines placed in a position away from cargo holds an pump rooms or by means of electric motors so designed, constructed and maintained as to be incapable of igniting inflammable vapour and maintained in accordance with Lloyd’s or any other approved classification society’s requirements.

44.	Matches. – No person engaged in landing or loading petroleum shall carry fuses, matches, or any other appliance for producing ignition or explosion.

45.	Fire-extinguishing appliances to be ready for use. – Vessels discharging or loading petroleum shall have adequate fire-extinguishing appliances so disposed that they can be put into immediate use, and, if the petroleum is dangerous petroleum shall have their awnings furled.

46.	Restriction on the conveyance of petroleum. – Dangerous and non-dangerous petroleum shall not be simultaneously conveyed to the shore or to another ship on the same vessel.

47.	Restriction as to leaky tins. – Leaky tins or other receptacles containing petroleum shall not be discharged into a vessel containing sound tins or other sound receptacles.

48.	Transport by sea of petroleum which has not been tested. – (1) Petroleum which has been imported into any port specified in sub-rule (1) of rule 7 and which not been tested at such port in accordance with the rules contained in Chapter IX, shall not be transported to any other port otherwise than to a port at which importation is permitted under sub-rule (1) of rule 7 and in accordance with the provisions of all the rules in Chapter II, except rule 5, when it arrives at such other port.

(2)	Nothing in sub-rule (1) shall apply to petroleum of Burmese origin which is covered by a certificate in Form B granted by a testing officer appointed by the Government of Burma.

49.	Transport by sea of petroleum which has been tested. – Petroleum which has been tested at one of the ports specified in sub-rule (1) of rule 7 and petroleum of Burmese origin which is covered by a certificate in Form B granted by a testing officer appointed by the Government of Burma, may be transported to any other port and the provisions of rule 8 to 14, 16 and 17 shall apply to such petroleum when it arrives at such other port.

50.	Omitted.

PART-III

COASTWISE TRANSPORT OF DANGEROUS PETROLEUM OTHERWISE THAN IN BULK.

51.	Applications. – (1) The rules in this part apply on to the transport coastwise and dangerous and dangerous petroleum otherwise than in bulk.

(2)	Unless otherwise expressly provided in this Part nothing contained in Part II of this Chapter, except rule 39, shall apply to any petroleum transported in accordance with this Part.

51-A.	Conditions of transport by un-berthed passenger ships. – Dangerous Petroleum may be transported otherwise than in bulk by an un-berthed passenger ship as defined in the Merchant Shipping Act, 1923 (XXI of 1923), not being a country craft, in accordance with the provisions of rule 35A and rule 53 to 61 inclusive.

52.	Maximum quantity allowed to be carried. – Dangerous petroleum may be transported otherwise than in bulk by country craft or steam or motor vessels other than un-berthed passenger ships as defined in the Merchant Shipping Act, 1923, subject to the provision of rule 53 to 62 inclusive, if the quantity of petroleum does not exceed.

- in the case of country craft, the licensed carrying capacity of the vessel after taking into account the weight of the barrels or tins in which the petroleum is carried ; or

- in the case of steam or motor-vessels, 15 tons.

53.	Loading of barrels and drums. – Barrels and drums shall be loaded with the bungs upwards.

54.	Carriage below decks. – Dangerous petroleum shall not be carried below decks in decked vessels unless the hold is properly ventilated.

55.	Provision of bulkhead. – In all vessels other than country craft a sold gas-tight bulkhead without openings, and in country craft a sold bulkhead without openings, shall be fitted between the hold and the after-deck where the crew are accommodated; and in vessels fitted with a poop the bulkhead shall be placed immediately in front of the poop. In decked vessels the bulkhead shall reach up to the deck ; in all other vessels it shall reach to within six inches of the gunwales.

56.	Fire, lights and smoking. – (1) No fire, naked light of any description and no smoking, shall be allowed on any part of vessel transporting dangerous petroleum except abaft the sold bulkhead.

(2)	The navigation light on any such vessel shall be carried abaft the bulkhead.

57.	Carriage of other inflammable cargo. – No inflammable cargo other than dangerous petroleum or other petroleum products or the dunnage used for packing purposes shall be carried on a vessel transporting petroleum.

58.	Fire buckets. – Buckets containing dry sand shall be placed at convenient points on a vessel transporting petroleum. Not less than two such buckets shall be placed on the after-deck.

59.	Construction of steam or motor-vessels. – Steam or motor vessels not specially constructed for the carriage of petroleum shall not carry petroleum unless they are constructed only of iron or steel.

60.	Transport in steam or motor-vessels. – On steam or motor-vessels, not specially constructed for the carriage of petroleum.  :-

- any petroleum shall either be carried in separate compartments which shall be gas-tight and shall be efficiently sealed, or in a hold in which there are efficient ventilators in accordance with clause (b), or on deck in accordance with rule 61 ;

- half of the ventilators provided in accordance with clause (a) shall extend to the bottom of the space, and the other half only a short distance, below the deck; the short ventilators shall be labeled “Inlet or to Windward”; such ventilators shall have large cowl heads, the openings being covered with double fine brass wire gauze;

- dangerous petroleum shall be contained in receptacles complying with the provision of rule 27 ; and

- special precautions shall be taken against smoking and the use of lights or fire of any kind while the cargo is being loaded or unloaded, or while the hatches are off, or any deck opening are uncovered; before any lights are used in a compartment which contains petroleum, precaution shall be taken to ensure that the space is clear of vapour; all empty receptacles which have contained dangerous petroleum shall be kept securely closed.

61.	Transport on deck. – Petroleum may be carried on deck in steam or motor vessels not specially built for the carriage of petroleum, subject to the following conditions:-

- in cargo ships dangerous petroleum shall not occupy more than 50 per cent of the open deck areas and shall be so stowed as not to interfere with the navigation of the ship, or make is unseaworthy ;

- in passenger ships a limited quantity of dangerous petroleum may be carried provided proper precautions are taken regarding stowage and keeping the packages away from passenger’s promenade or deck space;

- the petroleum shall be protected from the direct rays of the sun by the use of a canvas awning or otherwise; and

- conspicuous notices shall be posted up drawing attention to the danger arising from smoking or striking matches near the deck cargo.

62.	Conditions of transport by country craft. – No dangerous petroleum shall be transported in country craft except subject to the following conditions:-

- subject to the provision of rule 27, the petroleum shall be carried.

  - on 40/65 gallon steel barrels the screw bungs of such barrels being well-fitting and sealed; or

  - in 4 gallon sealed steel drums, not more than three tiers of which may be carried on any single vessel; or

  - in 2 gallon sealed steel tins, not more than six tiers of which may be carried on any single vessel;

- all barrels, drums or tins shall be placed within four feet of the after-deck where the crew are accommodated in the case of an un-decked vessel or on deck in the case of a decked vessel; and

- no passengers shall be carried on board the craft.

PART IV

TRANSPORT ON LAND VEHICLES

63.	Prohibition of fires and smoking. – (1) No fire or other artificial light capable of igniting inflammable vapour shall be allowed on any vehicle containing petroleum in bulk.

(2)	No person shall smoke while on or attending such a vehicle.

(3)	No article or substance capable of causing fire or explosion shall be carried on such a vehicle.

Explanation. – For the purposes of this rule any tank or other receptacle which has contained petroleum and which has not been thoroughly cleaned and freed from inflammable vapour shall be deemed to contained petroleum.

64.	Filling and discharge of tanks. – (1) Tanks-wagons, lorries or carts transporting petroleum shall only be filled or discharged by means of metal pipes or armoured hose in which the armouring is electrically continuous throughout.

(2)	Tanks, other than fuel tanks on vehicles, containing dangerous petroleum shall not be filled or discharged –

- within 100 feet of any fire, furnace or artificial light capable of igniting inflammable vapour; or

- at any place where the lorry, wagon or cart is exposed to sparks

Provided further that the distance specified in clause (i) may be reduced to the figure 12 feet prescribed in the license in Form K where the petroleum is filled, stored and discharged into a tank in any premises licensed in that Form:

Provided further that the distance specified in clause (i) may be reduced to three meters [10 feet] for LPG cargo vehicle unloading into the LPG storage container and so positioning that the shut-off valves in both the truck and container are readily accessible.

Explanation. – A pipe supplying liquid to a tank is “under seal” to that tank if it is screwed to the tank or otherwise attached so that no liquid or vapour can escape into the air except through an approved vent.

65.	Means of extinguishing fire to be carried. – An adequate supply of dry sand or other efficient means of extinguishing fire shall be carried in an easily accessible position on every vehicle transporting petroleum in bulk by road.

66.	Prohibition as to public service vehicle. – Petroleum shall not be transported on any public vehicle which is carrying passengers.

67.	Vehicle to be constantly attended. – Every vehicle on which petroleum is being transported by road, or which, while transporting petroleum by road is trailed by another vehicle, shall, so long as it contains petroleum, be attended by at least two persons:

Provided that such vehicles may be left unattended in places previously approved by the Chief Inspector.

68.	Trailers attached to vehicles transporting petroleum by road. – (1) A trailer not exclusively used for transporting petroleum shall not be attached to any vehicle transporting petroleum.

(2)	A trailer transporting petroleum shall not be attached to any vehicle other than a vehicle used for transporting petroleum, and not more than one trailer shall be so attached.

(3)	A trailer shall have two axles.

(4)	When a trailer is attached to a vehicle, the total quantity of petroleum transported on the trailer and the vehicle combined shall not exceed 2,000 gallons.

Provided that the Chief Inspector may, by order in writing and subject to such condition as he may deem fit to impose, raise the above limit to 3,000 gallons in the case of a tank wagon, and

(5)	If a trailer transporting dangerous petroleum is attached to a vehicle transporting non-dangerous petroleum, the vehicle shall comply with all the provisions of these rules relating to vehicles transporting dangerous petroleum.

(6)	A trailer other than a tank trailer shall not be attached to a tank-wagon. The capacity of a tank trailer shall not exceed 1,000 gallons, and no trailer shall be attached to a tank-wagon of greater capacity than 2,000 gallons.

(7)	No trailer attached to a tank-wagon shall be employed within any thickly populated area without the permission in writing of the District Authority.

69.	Tank capacity. – In these rules the tank forming part of a tank wagon or tank trailer shall be deemed to include any number of tanks on the same chassis and any limitation herein prescribed on the capacity of a tank shall be construed so as to permit of the tank containing the amount specified under varying degrees of temperature.

70.	Employment of electric light. – If electric lighting is employed on any vehicle, including a trailer, used in the transport of petroleum other than heavy petroleum by road, the following conditions shall be complied with :-

  - the pressure shall not exceed sixteen volts;

  - the circuit shall be heavily insulated and shall be independent of the chassis, and the wiring shall be so fixed and protected as to reduce as far as possible the risk of damage;

  - the generator, battery, switches and fuses shall be carried in front of the fire-resisting screen and the battery shall be in an easily accessible position; and

  - means of cutting off the current close to the battery by a double pole switch or other suitable method shall be provided.

71.	Fuelling from vehicles. – (1) No motor vehicle shall fill or replenish its fuel tanks with petroleum other than heavy petroleum directly from vehicles carrying petroleum in bulk.

(2)	Aircraft may receive fuel by means of specially constructed tank Lorries or wagons only if these are of a type approved by the Chief Inspector for this purpose.

(3)	During the fuelling of aircraft used for the conveyance of passengers no passenger shall be allowed to remain in the machine.

(4)	No person shall be allowed to smoke within 100 feet of any aircraft while it is being, or is about to be fuelled.

(5)	All aircraft engines within the distance specified in sub-rule (4) shall be stopped so long as fuelling is in progress.

(6)	Nothing is sub-rules (2) and (5) shall apply to military aircraft fuelling on military aerodromes.

72.	Owner responsible for observance of rules. – The owner of a vehicle used for the transport of petroleum who employs any person in connection with such transport, shall be responsible that all necessary measures have been taken to ensure that such person is acquainted with and carries out the provisions of these rules.

73.	Precautions to be observed during filling or emptying tank-wagons. – During the filling, discharging or emptying of any tank-wagon or trailer transporting petroleum in bulk other than heavy petroleum the following precautions shall be observed :-

- if the vehicle is mechanically-driven the engine shall be stopped so long as the filling, discharging or emptying is in progress and shall not be restarted until all tanks and valves have been securely closed.

Proved that this condition may be dispensed within the case of vehicles approved under sub-rule (2) of rule 71, which are supplying aircraft;

  - adequate provision shall be made to prevent the accumulation of a dangerous static charge of electricity.

- if the wagon is drawn by an animal or animals, they shall be removed from the wagon and the wheels securely scotched before the filling, discharging or emptying of any dangerous petroleum is begun; and

- the vehicle shall be constantly attended by a competent person.

74.	Composite vehicles. – Petroleum in cans or other receptacles shall not be transported by road on any tank-wagon used for the transport of petroleum unless the wagon is so constructed as to comply with the conditions applicable to transport on wagons other than tank-wagons as well as with the conditions applicable to transport on tank wagons.

75.	Filling and dipping pipes to be kept closed. – Except during the operation of filling or emptying a tank-wagon the filling and dipping pipes shall be kept securely closed. Where the filling pipes are not provided with a liquid seal, the covers shall be kept locked or properly sealed except during the operation of filling a tank-wagon, and the keys shall not be carried on the wagon.

76.	Filling and emptying by night. – Except where approved electric lighting as specified in rule 105 is exclusively used, the filling, discharging and emptying of tank-wagons shall be performed between the hours of sunrise and sunset.

77.	Approval of vehicles for transport in bulk necessary. – (1) Petroleum in bulk shall not be transported by land except in a vehicle approved [licensed] in writing by the Chief Inspector or Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf after physical inspection of vehicle and scrutiny of plan which shall be furnished, in triplicate, together with an original treasury receipt for Rs. 500, showing that the amount of fee has been deposited in the local treasury/bank under the head of account of Department of Explosives.

(1A)	Every approval accorded under sub-rule 1 may be revalidated by the authority empowered to accord such approval.

(1B)	Every application for revalidation of approval [license] shall be accompanied by the approved plan and original treasury receipt showing the deposit of fee of Rs. 500 under the correct head of account and shall be made so as reach the authority on or before the 2nd December each year.

(1C)	Application for revalidation of approval for tank lorry received after the 2nd December but not later than the 31st December shall be considered only on payment of double the fee ordinarily payable for such revalidation.

(2) 	All such vehicles other than those exclusively used for the transport of heavy petroleum shall have a stamped, embossed, painted or printed warning exhibiting in conspicuous characters the words “Petrol”, “Motor Spirit”, “Kerosene” or an equivalent warning of the nature of the contents.

(3)	Every such vehicle and its fittings shall be maintained in good condition.

78.	Vehicles for transport other than in bulk. – (1) Every vehicle on which petroleum not in bulk is transported shall be strongly constructed and with sides and back of adequate height and shall be maintained in good condition.

(2)	In the case of animal-drawn vehicles the requirement is sub-rule (1) regarding the sides and back of the vehicle shall not apply if the load is securely fastened to the vehicle.

(3)	All receptacles shall be so packed as not to project beyond the sides or back of the vehicle.

79.	Engines of mechanically-driven vehicles. – (1)  In every mechanically driven vehicle used for the transport by road of petroleum other than non-dangerous petroleum not in bulk or heavy petroleum :-

- the engine shall be of an internal combustion type;

- the engine fuel tank and electric batteries shall be effectively screened from the body of the vehicle by a fire-resisting shield carried up above the height of the load and down to within twelve inches of the ground; and

- the exhaust shall be wholly in front of the fire-resisting shield.

(2)	If the windows are provided in the fire-resisting shield they shall be fitted with wired glass.

(3)	The fuel tank of every such vehicle other than an articulated vehicle may be behind the fire-resisting shield if –

- a fuel feed apparatus, placed in front of the shield, is used to lift the contents from the fuel tank; and

- the fuel tank is protected from blows by the frame or by stout steel guards and the filling hole cover is provided with a lock.

(4)	The fuel tank of any vehicle may be behind the fire-resisting shield if the fuel used in the engine is heavy petroleum.

(5)	A quick action cut-off valve shall be fitted to the fuel feed pipe of every such vehicle in any easily accessible position, which shall be clearly marked.

80.	Speed limit for vehicles. – Without prejudice to the operation of any other provision of law for the time being in force whereby a lower limit of speed is imposed, the speed of a motor tank wagon or a motor lorry transporting petroleum in receptacles shall not exceed 30 miles per hours if fitted with solid tyres.

81.	Exemptions. – (1) If the Chief Inspector is satisfied that in respect of any class of vehicle any of the requirements of rules 68, 78 and 79 may be safely suspended or relaxed, he may authorize such suspension or relaxation for such period and under such condition as he may think fit.

(2)	Nothing in rules 68, 70, 77, 78 and 79 shall apply to vehicles and trailers in the possession of Armed Forces of Pakistan.

82.	Special provision of motor conveyances. – (1) Rules 63 to 80 shall not apply to the conveyance of petroleum in any motor vehicle for use only in the propulsion of such vehicle.

(2)	No motor conveyance carrying passengers on hire shall carry any petroleum other than :-

- petroleum in the fuel tank incorporated in the conveyance, and

(ii)	petroleum not exceeding 20 gallons in quantity intended to be used to generate motive power for the conveyance and kept in the manner provided in sub-section (2) of section of the Act.

(3)	During the filling or replenishment of the fuel tank of a vehicle licensed for conveyance of more than six passengers on hire, the driver or other person in charge of the vehicle shall not allow any passenger to remain in the vehicle.

(4)	All petroleum tins carried in a vehicle carrying passengers for hire shall be securely closed and shall be carried in a specially prepared receptacle which is not accessible to passengers in the vehicle and is not on the roof.

PART V

TRANSPORT BY PIPE LINES

83.	Application. – The rules in this part apply only to the transport of petroleum by means of pipe lines other than those in any area in which operations for the winning of natural petroleum or natural gas or both are carried on or within the limits of refineries and installations.

84.	Casing. – (1) An approved casing shall be put over the pipe line where it passes under any railway or public road and an approved protective casing shall be constructed round the pipe where it crosses over any railway or protected work

Provided that the Chief Inspector may require an extra casing to be put over the pipe line where it crosses any steam, road, railway or protected work.

85.	Patrol. – The whole of every pipe line shall be efficiently patrolled.

86.	Prevention of excessive pressure. – As a precaution against excessive pressure in the pipe line, an automatic by-pass relief valve and a reliable pressure gauge shall be placed on the common discharge pipe at pumping station.

87.	Telegraph and telephone. – A telephone or telegraph line shall be provided with connections at frequent intervals along the pipe line. One telephone or telegraph lien shall suffice for a series of parallel pipe lines.

Provided that this rule shall not apply to a pipe line connecting railway siding with installations if the length of such pipe line does not exceed one mile.

88.	Gate valves. – Gate valves shall be provided at reasonable intervals.

89.	Checking of tank gauges. – Tank gauges shall be checked between stations at frequent intervals.

CHAPTER IV

Storage of Petroleum Requiring License

90.	License for storage. – Save as provided in section 7, 8 and 9 of the Act and by rule 109 no one shall store any petroleum except under a license granted under these rule

Provided that no licence shall be necessary for storage in a well-head tank.

91.	Precautions against fire. – (1) No person shall smoke in any installation or storage shed.

(2)	No person shall carry matches, fuses or other appliance for producing ignition or explosion in any installation or storage shed which is used for the storage of dangerous petroleum.

(3)	No fire, furnace or other source of heat or light capable of igniting inflammable vapour shall be allowed in any licensed installation or storage shed save in places specially authorized by the licensing authority for the purpose.

(4)	An adequate supply of dry sand or earth together with the necessary implements for its convenient application, or other efficient means of extinguishing petroleum fires, shall always be kept in every installation and in or adjacent to every storage shed.

92.	Supervision of operations within an installation or storage shed. – All operations within an installation or storage shed shall be conducted under the supervision of an experienced responsible agent or supervisor.

93.	Cleanliness of installation or storage shed. – The ground in the interior of an installation, and the protected area surrounding any storage shed or installation shall be kept clean and free from all inflammable material, waster vegetation and rubbish.

Explanation. – In this rule “protected area” means the areas necessary for the maintenance of the distances required and the conditions of the license to be kept clear between any installation or storage shed and any protected work.

94.	Drainage. – (1) All enclosures surrounding tanks or buildings belonging to an installation or storage shed shall be kept drained and no water shall be allowed to accumulate in the enclosure.

(2)	Where drainage is affected by means of a pipe, the pipe shall be fitted with a valve actuated from the outside of the enclosure:

Provided that this sub-rule shall not apply to storage sheds which are not required under these rules or the terms of the license to be provided with an enclosure wall or embankment.

(3)	All valves and other openings for draining off water shall be kept closed except when water is being drained off.

(4)	The nature of the drainage arrangements shall be shown in the plan submitted with the application for the license.

95.	Exclusion of unauthorized persons. – (1) Every installation shall be surrounded by a wall or fence of at least six feet in height:

Provided that nothing in this sub-rule shall apply to an installation licensed under the rules in force immediately before these rules come into operation unless its fencing is considered by the licensing authority to be unsatisfactory:

Provided further that the Chief Inspector may waive this sub-rule in the case of an installation connected with a pump outfit and floating storage barges, under such conditions as he deems necessary.

(2)	Precaution shall be taken to prevent unauthorized persons from having access to any storage shed or installation.

96.	Children. – No persons under the age of 15 years shall be employed in or allowed to enter any premises licensed under these rules.

97.	Receptacles for petroleum. – The provisions of rules 26, 27, and 28 shall apply to petroleum stored under license.

98.	Petroleum only to be stored. – No installation or storage shed shall without permission in writing from the Chief Inspector be used for any purpose other than the storage and distribution of petroleum and purposes directly connected therewith.

98A. Approval of ancillary facilities. – The pump premises for the approval of ancillary facilities shall conform to the minimum standard as laid down in Schedule IV at the end of these rules.

99.	Marking of capacity of tanks. – The capacity in gallons of every tank in an installation shall be conspicuously marked in the tank.

The “capacity” of the tank is to be calculated and marked according to the nature of the petroleum proposed to be stored therein leaving margin for air-space prescribed in the Rules. The object of this provision is to ensure that the capacity thus marked constitutes the actual licensable capacity of the tank.

100.	Construction of tank. – Every tank or other receptacle used for the storage of petroleum in bulk other than well-head tank shall be constructed of iron or steel properly erected and designed according to sound engineering practice and, together with all pipes and fittings shall be so constructed and maintained as to prevent any leakage of petroleum.

101.	Testing of tanks. – (1) Storage tanks or other receptacles for the storage of petroleum in bulk other than well-head tanks, after being placed in a final position and before being brought into use, shall, unless they were in use before the 1st April 1937, be tested by water pressure by the licensee in the presence of an Engineer accepted as qualified for the purpose by the licensing authority.

(2)	The water used for testing shall be free from petroleum and shall not be passed through any pies or pumps ordinarily used for the conveyance of petroleum :

Provided that, where the licensing authority is satisfied that it is not reasonably possible to convey water by pipes or pumps other than those ordinarily used for the conveyance of petroleum, he may permit the use of a petroleum-pipe or pump for the conveyance of water subject to such condition as he may impose.

(3)	The test referred to in sub-rule (1) shall also be made before any receptacles for the storage of petroleum in bulk are brought into use after being repaired.

102.	Earthing of tanks. – All tanks or other receptacles for the storage of petroleum in bulk other than well-head tank or tanks for receptacles of less than 10,000 gallons capacity containing heavy petroleum shall be electrically connected with the earth in an efficient manner by means of not less than two separate and distinct connections placed at opposite extremities of such tank or receptacles. The roof and all metal connections of such tank or receptacle shall be in efficient electrical contact with the body of such tank or receptacle.

103.	Inspection of earth connection. – (1) The connections and contacts required by rule 102 shall be inspected and tested at least once in every year by an Inspector or Assistant Inspector of Explosives in the manner prescribed by the Chief Inspector.

(2)	The inspection under this rule should be carried out in the following manner:-

- Examine visually all joints and connections above ground to discover if any of these are loose or disconnected. The number of joints should be as few as possible but where they are necessary they should be properly soldered as well as riveted to ensure both mechanical and electrical soundness.

(ii)	The electrical resistance to earth should be tested and measured either by means of a direct reading instrument or by the procedure laid down in the “Code of Instruction for the Guidance of Public Works Officers in the Erection and Testing of Lightning Conductors”.

(iii)	The conditions of the connections and contacts will not be considered satisfactory unless the resistances to earth are found to be less than 10 ohms.

CAUTION: - The use of any testing instrument, capable of producing a spark, which is not so shielded as to be incapable of igniting inflammable vapours, is prohibited under Rule 91.

(3)	A fee of one hundred rupees, for the service, shall be payable by the licensee for the test prescribed in Rule 103(1). In the event of the test proving unsatisfactory a fee of fifty rupees shall be payable by the licensee for each subsequent test until the circuit is passed by the Testing Officer as satisfactory:

Provided that (1) not more than one hundred rupees shall be charged for all tests made on a circuit during any one day; and

(2)	where two or more earthing circuits are connected to the same tank, fee for testing all such circuits shall not exceed the fee prescribed for testing one circuit.

The Inspection under this Rule should be carried out in the following manner:-

(1)	Examine visually all joints and connections above ground to discover if any of these are loose or disconnected.

(2)	While testing an individual earth connection other connection fitted on the object should be disconnected. The electrical resistance to earth should be tested and measured either by means of a direct reading instrument or by the procedure laid down in the “Code of Instruction for guidance of Public Works Officers in the erection and testing of lightning conductors”. The “British Standard Code Practice C.P. 326.101(1948)” may be consulted for further details.

(3)	Earth resistance should not ordinarily exceed 1 ohm though 10 ohms is the permissible limit.

(4)	The test record should be maintained in the following form:

Name of the licensee.  _____________________

License No.                 _____________________

Tank No.                     _____________________

Date of inspection.      _____________________

Resistance in ohms in each connection:

- First reading,      _____________________

- Second reading,  _____________________

- Third reading,     _____________________

- Mean (average).  _____________________

Weather report for the previous week. ___________________________

Nature of the soil.                                 ___________________________

104.	Night working. – No installation or storage shed shall be open, and no work in any installation or storage shed shall be permitted, between sunset and sunrise except where approved electric lighting as specified in rule 105 is exclusively used.

105.	Electric apparatus. – (1) All electric wires installed at less than 15 feet from the ground in any petroleum installation or situated within 20 feet of any building or tank containing dangerous petroleum shall consist of insulated cables, enclosed in metallic coverings which shall be gas-tight, electrically and mechanically continuous throughout, and effectively earthed outside the building.

(2)	No electric wire shall pass over any petroleum tank, filling, painting or storage shed.

(3)	In filling, painting and storage sheds and pump rooms used for – (i) dangerous petroleum –

- all electric meters, distribution boards, switches, fuses, plugs and sockets shall be placed outside the building and shall be of flame-proof construction satisfying the requirements of the British Standard Specification No. 229, and the frame shall be effectively earthed;

- all electric fixed lamps shall be enclosed in a well glass flame-proof fitting, either double enclosed with an inner and an outer well glass or singly enclosed with substantial metal protection ; such lamps shall be installed at 12 feet where possible, but in no case less than 8 feet, above the floor level;

- all electric portable hand lamp of the self-contained pattern shall be of a type approved by the Chief Inspector.

- for the examination of cans and other containers, electric torches employing a separate battery may be used; these torches shall be fitted with substantially protected flame-proof globes and shall be supplied through a cable of cab-tyre or other suitable sheathing and properly constructed flame-proof connectors; and

- no single fixed lamp shall exceed 150 watts.

(ii)	non-dangerous petroleum:-

- all electric meters, distribution boards, switches, fuses, plugs and sockets shall be enclosed in iron-clad, gas-tight cases and shall be fixed at least 5 feet above the floor level in well-ventilated positions close to the door;

- all electric fixed lamps shall be enclosed in a gas-tight well glass fitting provided with substantial metal protection;

- all electric portable hand lamps shall be fitted with substantially protected gas-tight globes and supplied through a flexible cab-tyre or other suitable sheathing and properly constructed gas-tight connectors; and

- no single fixed lamp shall exceed 200 watts and no hand lamp shall exceed 30 watts.

106.	Pumping. – No internal combustion engine or electric motor shall be used for driving pumps for pumping petroleum save in a pump house specially constructed for the purpose and under such conditions as may be approved by the Chief Inspector.

Provided that this rule shall not apply where the motor, control switchgear and starting apparatus are of flame-proof construction satisfying the requirements of the British Standard Specification No. 229.

107.	Posting up of rules and conditions. – Copies of the preceding rules in this Chapter and of the conditions of the license shall be exhibited in a conspicuous place in very licensed installation and storage shed.

108.	Petroleum in possession of the Armed forces of Pakistan. – Nothing in rules 90, 95, 98, 101 and 104 shall apply to petroleum in the possession of the Armed Forces of Pakistan.

CHAPTER V

Storage of Petroleum not Requiring License

109.	Exemption of heavy petroleum. – (1) Notwithstanding anything contained in these rules, it shall be permissible to store without license, subject to the conditions of this Chapter, heavy petroleum in quantities not exceeding 10,000 gallons, which is not stored in the same installation or storage shed as other petroleum.

(2)	The provisions of Chapter IV shall not apply to petroleum so permitted to be stored without license under sub-rule (1).

(3)	The exemption under sub-rule (1) above shall not apply to the storage of any kind of petroleum in any quantity in bulk stored in a tank connected with a pump outfit for fueling motor vehicles which will be licensed in Form ‘K’.

110.	Storage of exempted heavy petroleum in bulk. – (1) Heavy petroleum in bulk, if stored otherwise than under a license, shall be stored in tank constructed of iron or steel properly erected and designed and the tank with all pipes and fittings shall be so constructed and maintained as to prevent any leakage of petroleum.

(2)	All tanks of a capacity exceeding 1,000 gallons shall be surrounded by bank or wall, or sunk in a pit, so constructed and maintained as to be able to contain without leakage the whole of the petroleum liable to be present at any time in the tank.

(3)	A distance of not less than ten feet shall be kept clear between protected works and the enclosure walls or banks.

(4)	Nothing in this rule shall apply to petroleum in the possession of Armed Forces of Pakistan.

111.	Storage of exempted heavy petroleum not in bulk. – Heavy petroleum which is not in bulk, if stored otherwise than under a license, shall, if the quantity exceeds 500 gallons, be stored in a storage shed of which either –

- the doorways and other opening shall be built up to a height of one foot above the level of the floor; or

- the floor shall be sunk to a dept of one foot.

112.	Prior report of storage of exempted heavy petroleum. – Every person intending to store heavy petroleum in quantity exceeding 1,000 gallons otherwise than under a license shall send to the Chief Inspector a prior report stating the situation of the premises on which such petroleum is to be stored.

113.	Garages and hangars. – (1) Every garage or hangar used for housing any motor conveyance containing dangerous petroleum in bulk in any tank incorporated in the conveyance, whether such petroleum is intended to be used to generate motive power for the conveyance or not, shall be constructed of un-inflammable material and be effectively and safely ventilated to the open air.

(2)	Every such garage or hangar shall be in charge of a competent person who shall be responsible for taking all proper precautions against fire and shall prevent unauthorized person from having access to the building.

CHAPTER VI

Licenses

114.	Application for license. (1) A person wishing to obtain or to renew a license prescribed under these rule shall submit an application in writing to the authority empowered to grant such a license.

(2)	Every application for the grant or renewal of a license to store or to import and store petroleum shall be in Form D.

115.	Grant of license. – (1) Licenses for importation and storage may be granted by the licensing authorities set forth in Schedule I in the forms, for the purposes, and on payment of the fees, specified therein.

(2A)	Notwithstanding anything contained in sub-rule (2), the licensing authority may, if it is satisfied that a license is required for specific work of national importance and for a short period, grant a license for a period not exceeding three months but not extending beyond the 31st December, following the date on which the license is granted: Provided that an Inspector of Explosives shall not grant such a license without the concurrence of the Chief Inspector of Explosives if a Certificate is not obtained from the District Authority under sub-rule (3)” and

(2)	A license in form H may be granted for such period as the licensing authority may deem necessary subject to a maximum of twelve months. Every other license granted or renewed under these rules shall remain in force until the 31st day of December of the year for which the license is granted or renewed.

(3)	Where the licensing authority is the Chief Inspector or an Inspector of Explosives an applicant for a new license may apply to the District Authority for a certificate to the effect that there is no objection to the applicant receiving a license for the site proposed and the District Authority shall, if he sees no objection, grant such certificate to the applicant who may forward it to the Chief Inspector or an Inspector of Explosives with his application in Form D.

(3A) Where the site proposed is located in the port land and includes loading and unloading facilities, the Port Authority, while granting the certificate under sub-rule (3), shall endorse on the plan accompanying the application the details of the loading and unloading facilities keeping in view the requirements of safety distance as laid down in the relevant rules made for the port.

(4)	The Chief Inspector or the Inspector of Explosives may refer an application not accompanied by a certificate granted under sub-rule (3), to the District Authority for his observations.

(4A) Nothing in sub-rule (3) or sub-rule (4) shall be deemed to require an application for the grant of a license for a site for which a license was previously granted and has expired to be accompanied by a certificate granted under the said sub-rule (3).

(5)	If the District Authority, either on a reference being made to him or otherwise, intimates to the Chief Inspector or the Inspector of Explosives that any license which has been applied for should not in his opinion be granted, such license shall not be issued without the sanction of the Central Government.

(6)	No license in Form H shall be granted except to a person holding a license in Form I.

(7)	In the case of license granted for storage one copy of the plan or plans of the storage premises signed in token of approval by the licensing authority shall be attached to the license and one copy shall be filed for record in the office of the licensing authority.

(8) If the site proposed is located on land within the jurisdiction of a Port Authority or the Civil Aviation Authority, reference in this rule to District Authority shall be construed as reference to Port Authority or Civil Aviation Authority, as the case may be.

(9) For installation of a CNG station at any existing petrol pump, no additional NOC shall be required except permission for construction and installation and license for its operation from the Department of Explosives.

(10) For installation of a stand alone CNG station at raw sites or new location, NOC’s from the following authorities shall be required, namely:-

  - Gas Utility Company;

  - Civil Defense; and

  - Tehsil Municipal Officer.

(11)     The permission for construction and installation of CNG station along with plan approval shall be granted by Chief Inspector of Explosives under the Petroleum Act, 1934 (XXX of 1934) and the Explosives Act, 1884 (IV of 1884).

(12) All authorities concerned for issuance of permission or NOCs or licenses or otherwise shall decide the case within one month of the receipt of the request for installation of a CNG station

116.	Particulars of license. – Every license granted under these rules shall be held subject to the conditions endorsed on it and shall contain all the particulars which are contained in the form prescribed for it by these rules.

117.	Power of licensing authority to alter conditions. – (1) Notwithstanding anything contained in rule 116 the licensing authority, at the time of issuing a license may omit, alter or add to any of the conditions specified in the prescribed form of license.

(2)	The power conferred by sub-rule (1) shall not be exercised by any licensing authority other than the Chief Inspector of Explosives.

118.	Amendment of license. – (1) Any license granted under these rules may be amended by the authority granting such a license:

Provided that the amendment shall not be inconsistent with any rule in this Chapter.

(2)	A licensee who desires to have his license amended shall submit it to the licensing authority with an application stating the nature of the amendment and the reason therefore.

(3)	The fee for the amendment of a license shall be twenty five rupees plus the amount (if any) by which the fee that would have been payable if the license had originally been issued in the amended for exceeds the fee originally paid for the license.

119.	Renewal of license. – (1) A license may be renewed by the authority empowered to grant such a license, provided that a license which has been granted by the Chief Inspector may be renewed without alteration by an Inspector or Explosives duly authorized by the Chief Inspector in this behalf.

(2)	Every application for the renewal of a license shall be made to as to reach the licensing authority not less than thirty days before the date on which the license expires, and, if the application is so made, the premises shall be held to be duly licensed until such date as the licensing authority renews the license or until an intimation that the renewal of the license is refused has been communicated to the application.

(2A)	Every application under sub-rule (2) shall be accompanied by the license which is to be renewed together with the approved plan attached thereto and the original treasury receipt showing the deposit of the correct renewal fee under the correct head of account.

(3)	The same fee shall be charged for the renewal of license as for the grant thereof, provided that if the application for renewal is not received within the time specified in sub-rule (2), the license shall be renewed only, on payment of double the fee ordinarily payable for the license.

120.	Refusal of license. – (1) A licensing authority refusing to grant, amend or renew a license, shall record his reason for such refusal in writing.

(2)	A copy of the order containing the reason for such refusal shall be given to the applicant on payment of a fee of rupees twenty five.

121.	Suspension or cancellation of license. – (1) Every license granted under these rules shall be liable to be suspended or cancelled by order the licensing authority for any contravention of the Act or of any rule thereunder, or of any condition contained in such license.

(2)	A licensing authority suspending or canceling a license shall record his reason for so doing in writing.

(3)	A copy of the order containing the reasons for the suspension or cancellation of a license shall be given to the holder of the license on payment of a fee of rupees twenty five.

122.	Appeals. – (1) An appeal shall lie against any order refusing to grant, amend or renew a license or suspending or canceling a license –

(i)	to the Central Government where the order is passed by the Chief Inspector;

- to the immediate official superior to the District Authority if the order is passed by the District Authority; and

- to the Chief Inspector if the order is passed by an Inspector of explosives.

(2)	Every appeal shall be in writing and shall be accompanied by a copy of the order appealed against and shall be present within 60 days or the order passed if preferred to the Central Government, and within 30 days in all other cases.

123.	Supply of rules. – With every license granted for the storage of petroleum, a copy of rule 90 to 107 in Chapter IV, shall be given free of charge to the licensee.

124.	Certificate of safety. – (1) Before petroleum is stored in any installation, for which a license is being granted for the first time, a certificate shall be furnished to the licensing authority to the effect that all enclosure walls and embankments constructed in accordance with the condition of the license are of such a nature as to ensure safety.

(2)	The certificate shall be signed by an Engineer accepted as qualified for the purpose by the licensing authority.

(3)	When the license is not granted for the first time, but is being granted for the increased quantity of petroleum, a certificate shall similarly be furnished to the licensing authority before any quantity of petroleum exceeding the amount which was admissible under the former license is stored in the installation.

I hereby certify that the dangerous/non-dangerous petroleum installation of ………………………………………….. at ………………………………. has been constructed in accordance with the conditions of the license and that in my opinion the enclosure walls and embankments are of such a nature as to ensure safety.

Signature.………………………..

Designation………………………

Place……………………….

Date………………………..

125.	Transfer of license for storage. – (1) The holder of a license for the storage of petroleum may, at any time before the expiry of the license, apply for permission to transfer his license to another person.

(2)	Such application shall be made to the licensing authority who shall, if he approves of the transfer, enter upon the license, under his signature, an endorsement to the effect that the license has been transferred to the person named.

(3)	A fee equal to the license fee shall be charged on each such application.

(4)	The person to whom the license is so transferred shall enjoy the same power and be subject to the same obligations under the license as the original holder.

126.	Procedure on death or disability of licensee. – (1) If a licensee dies or becomes insolvent or mentally incapable or otherwise disabled, the person carrying on the business of such licensee shall not be liable to any penalty or confiscation under the Act or these rules for exercising the powers granted to the licensee by the license during such time may reasonably be required to allow him to make an application for a new license in his own name for the unexpired portion of the original license.

(2)	A fee equal to the license fee shall be charged for a new license for the unexpired portion of an original license granted to any person applying for it under this rule.

127.	Loss of license. – Where a license granted these rules is lot or accidentally destroyed a duplicate may be granted on payment of a fee of fifteen rupees.

128.	Payment of fees. – (1) Every application under this Chapter shall be accompanied:-

- If in respect of a license granted or to be granted by the District Authority, by the appropriate fee in cash or by cheque, and

(ii)	if in respect of any other license, by a Treasury receipt showing that the appropriate fee has been paid into the local Treasury under the Department of Explosive’s head of account:

(2)	If an application for the grant, renewal or amendment of a license is rejected, the fee paid shall be refunded by the District Authority, or if it has been paid into a Treasury, by that Treasury on the production of a signed order from the licensing authority directing such refund.

(3)	Fees payable under any other Chapter of these rules shall be paid in cash or by cheque.

128a. Time Limit for Payment of Fees for un-authorized or excess storage.-

The fee assessed for payment in respect of un-authorized or excess storage shall be paid within 30 days of the receipt of demand letter. If the fee is not paid within the period specified, an amount equal to double the fee ordinarily payable under these rules shall be payable within 30 days following that period.

129.	Power to exempt from payment of fees. – The Central Government may, by general or special order, grant exemption from or reduction of any fee payable under these rules.

130.	Production of license on demand. – (1) Every person holding or acting under a license granted under these rules shall produce it, or an authenticated copy of it, at the place to which the license applied, when called upon to do so by an Inspector.

(2)	Copies of any license may, for the purposes of this rule, be authenticated by the licensing authority on payment of twenty five rupees for each authentication-Duplicate authenticated copy may be issued on payment of fifteen rupees for each license.

131.	Procedure on reports of infringements. – The District Authority shall inform the Chief Inspector of the action taken by him on any reports of infringements or the Act or of these rules, which the Chief Inspector may make to him.

131A. Executive control over authorities. – Every authority other than the Central Government acting under this Chapter shall perform his duties subject to the control of the Central Government:

Provided that nothing in this rule shall be deemed to affect the powers of executive control of the Chief Inspector over the officers subordinate to him.

CHAPTER VII

Refining and Blending of Petroleum

132.	Approval of refinery. – (1) No person shall refine or blend petroleum unless the plans showing the general arrangement of tanks, stills, fencing, gates, and all plant and buildings at the place where it is proposed to refine or blend petroleum (hereinafter in this Chapter referred to as the refinery) have been approved by the Chief Inspector.

(2)	The Chief Inspector on receiving an application under sub-rule (1) may require the submission of such particulars as he may specify regarding the materials used or to be used in the construction of stills, condensing pipes and tanks, and the method of their erection.

133.	Retention of plans. – A copy of the approved plans, which shall incorporate any alteration sanctioned under rule 135 from time to time, shall be kept at the refinery.

134.	Application of rules. – Rules 135 to 147 inclusive apply on to refineries.

135.	Alternations. – No alteration in a refinery involving the general arrangement of tanks, stills, any other plant and buildings or the materials used in the construction of the method of erection of the stills, condensing pipes and tanks shall be carried out without the previous sanction in writing of the Chief Inspector.

136.	Use of fire-proof materials. – All building in which petroleum is handled shall be built of fire-proof materials.

137.	Situation of storage tanks. – No storage tank, the capacity of which exceeds 50,000 gallons, shall be situated nearer than 300 feet to any still, boiler or furnace.

138.	Size of service tanks. – Unless specially permitted by the Chief Inspector service tanks (i.e., tanks which contain fuel for boiler and still fires) shall not be larger than is necessary to conserve 24 hours fuel for the fire which they serve.

139.	Drainage. – Suitable arrangements shall be made for the proper carrying of and fire-trapping of all drainage and possible leakage from a still or bench of stills.

140.	Fires and smoking. – (1) No fire, furnace or source of heat or light capable of igniting inflammable vapour shall be allowed except in the firing spaces of still or boilers.

(2)	No smoking shall be allowed except in spaces or buildings specially approved for the purpose by the Chief Inspector.

141.	Supply of sand or earth. – (1) An adequate quantity of dry sand or earth together with the necessary implements for its convenient application or other efficient means of extinguishing petroleum fires shall always be kept readily accessible near tanks and stills.

(2)	The Chief Inspector may specify the quantity of dry sand or earth which shall be deemed to be adequate for the purposes of this rule.

142.	Hydrants and hoses. – (1) In a refinery with still capacity exceeding on an average 1,000 gallons daily, hydrants with a minimum pressure of 40 lbs. with the necessary hose, shall be provided at suitable points. Their location shall be shown in the approved plan of the refinery.

(2)	All hydrants and hose shall be kept in an efficient condition.

143.	Pumping of dangerous Petroleum. – All dangerous petroleum as it leaves the stills, with the exception of such quantities as may be pumped direct to service tanks for fuel, shall be at once pumped out of the refinery to storage tanks, and shall not be stored in the immediate neighbourhood of stills and boiler:

Provided that the Chief Inspector may permit dangerous petroleum to be disposed of otherwise.

144.	Prevention of danger from electricity. – Adequate provision shall be made to prevent the accumulation of dangerous static charges of electricity.

145.	Plans. – Fire walls and efficient separators for drainage shall be shown in the plans referred to in rule 132 and may be required to be erected when deemed necessary by the Chief Inspector.

146.	Reports of fires. – The occurrence of any fire at a refinery shall be reported immediately by the person in charge of the refinery for the time being to the nearest Police Station and to the Chief Inspector.

147.	Closing of refinery. – If a refinery is closed down, the area within the fence surrounding it shall be cleared of all petroleum having a flashing-point below 200 degree F, as soon as possible.

CHAPTER VIII

Tetra Ethyl Lead Mixture

148.	Addition of tetra ethyl lead. – Tetra ethyl lead shall not be blended with petroleum except in equipment approved in writing by the Chief Inspector and in such proportions and under such conditions as may from time to time be determined by him.

149.	Importation, Transport and Storage. – No person shall import, transport or store petroleum containing tetra ethyl lead unless the proportions of tetra ethyl lead have been previously determined by the Chief Inspector in accordance with rule 148.

150.	Prescription of special conditions. – The Chief Inspector may from time to time by a written order prescribe special conditions which shall be observed during handling of leaded petroleum or cleaning or repair of storage tanks which have contained leaded petroleum.

151.	Colouration. – Every mixture of petroleum and tetra ethyl lead shall be distinctly colored before being supplied to the public.

152.	Marking of receptacles. – All receptacles containing a mixture of petroleum and tetra ethyl lead in non-bulk, other than tanks on tank carts, shall unless they are in the possession of the Armed Forces of Pakistan bear a warning in the following terms –

“Warning

This spirit contains lead and should be used as a motor fuel only”

CHAPTER IX

Testing of Petroleum

153.	Drawing of samples. – (1) In all cases the sampling officer shall personally superintend the drawing of the sample. Where the sample is drawing from an original unopened receptacle containing petroleum not in bulk the opening shall be sufficient to admit of the sample being rapidly transferred from the receptacle.

(2)	Two bottles, each of the capacity of about 40-fluid ounces, shall be filled to three-quarters of their capacity with the sample and corked. The corks shall be driven home and cut off level with the neck; and melted sealing wax shall be worked into the corks and the bottles shall be efficiently sealed.

(3)	In the case of petroleum imported by sea the bottles containing the sample shall, after being sealed, be labeled with the name of the ship, the name of the consignee and such other distinguishing marks as may be necessary.

154.	Forwarding and retention of samples. – One of the bottles referred to in sub-rule (2) of rule 153 shall be preserved for reference in case of need and the other shall be forwarded to the testing officer.

155.	Procedure of delivering of samples from ship’s cargo. – (1) When the master of, or the agent for, a ship has made the declaration required by rule 8, the sampling officer shall go on board the vessel and obtain samples of all the petroleum on board which it is intended to land at the port. If the importer so desires the sampling officer shall also take samples of all the petroleum on board which it is intended to land at any other port in Pakistan:

Provided that no sample need be taken of –

- petroleum which is declared to be dangerous; or

- petroleum of Burmese origin which is covered by a certificate in Form B granted by testing officer appointed by the Government of Burma.

(2)	The master shall delivery to the sampling officer, without charge, samples of every variety of petroleum comprised in the petroleum of which samples are to be taken under sub-rule (1). Such samples shall, if the sampling officer so requires, be taken from the particular receptacles indicated by him:

Provided that when the petroleum is in cases, samples may be taken as landing proceeds.

156.	Selection of samples from ship’s cargo. – The minimum number of samples to be selected of each brand of quality contained in the cargo shall be as follows:-

(a)	of petroleum certified in accordance with 11 –

- in cases – one sample for every 15,000 cases or part thereof;

- in casks of drums, declared to be of uniform quality – one sample for every 120,000 gallons or part thereof;

- in bulk or in tanks – one sample from each group of tanks or tank compartments certified to be of the same brand or quality.

- of other petroleum –

  - in cases – one sample for every 10,000 cases or part thereof;

  - in casks or drums, declared to be of uniform quality – one sample for every 80,000 gallons or part thereof;

  - in bulk or in tanks – one sample from each tank or tank compartment.

157.	Standard Test Apparatus. – (1) The Standard Test Apparatus and thermometers shall –

  - agree in every respect with the specifications laid down in Schedule III; and

  - have been tested and certified by the Board of Trade or the National Physical Laboratory, London, and marked with the year of test.

(2)	The standard thermometers shall be replaced at least once in every three years.

158.	Certificate of apparatus. – (1) When any apparatus for determining the flashing-point of petroleum is submitted to the officer appointed under sub-section (1) of section 15 of the Act for comparison with the Standard Test Apparatus, that officer shall examine the apparatus including the thermometers and the barometers or aneroids.

(2)	No certificate shall be granted under section 16 of the Act if –

- the apparatus is in any respect outside the tolerances laid down in Schedule III to these rules or is otherwise defective; or

- any thermometer shows reading varying by more than 1 deg F, at temperature of 76 deg F, and 120 deg F as given by the Standard Test Apparatus; or

- any barometer or aneroid shows a variation of more than half an inch from the pressure given by the Standard Test Apparatus.

(3)	A certificate in Form E shall be granted in respect of any apparatus which has been found to agree with the Standard Test Apparatus within the limits mentioned in sub-rule (2).

(4)	A certificate granted under this rule shall be valid for a period of three years.

159.	Register of certificates. – A register of all certificates granted under rule 158 shall be maintained in Form F by the officer appointed under sub-section (1) of section 15 of the Act.

160.	Methods of test. – (1) The testing officer shall test the samples in the manner laid down in Schedule III to these rules.

(2)	In all cases at least three samples shall be separately test, the average of three readings being corrected for the thermometer correction, if any, and for the barometric correction in case of dispute.

(3)	If the average flashing-point is not lower than 76 deg F and no one test give a flashing-point below 73 deg F the whole of the petroleum represented by the samples shall be deemed to be non-dangerous petroleum.

161.	Procedure when test shows want of uniformity. – (1) If the testing officer after testing samples taken from a ship’s cargo, considers further tests necessary to satisfy himself that none of the petroleum is dangerous, he shall report to the Collector of Customs accordingly.

(2)	On receipt of a report under sub-rule (1) –

- when the consignment is imported in cases or casks or drums, the Collector of Customs shall cause the petroleum in question to be landed and stacked in lots of not more than 1,500 cases or casks or drum each, or to be discharged into boats each containing not more than 1,500 cases or casks or drums, and the sampling officer shall select and delivery to the testing officer one sample from each lot;

- when the consignment is imported in bulk, the sampling officer shall forward a second sample and the Collector of Customs may, until the receipt of the testing officer’s further report, prevent the landing of any portion of the contents of the tan k in question, or may permit it to be landed as provided in rule 15;

- if the petroleum has been already landed and stored under rule 15 –

  - if it is not in bulk it shall be divided into lots and samples of each lot shall be selected as provided in clause (a);

  - if it is in bulk samples shall be drawn from each separate storage tank containing the petroleum.

162.	Certificate of tests. – (1) The testing officer shall as soon as practicable and ordinarily within twenty-four hours after receipt of any samples make out a certificate in form G and shall forward it in the case of samples of petroleum taken on board a ship to the Collector of Customs and in the case in the other samples to the officer submitting the sample.

(2)	The testing officer shall, at the request of any person concerned, furnish him with a certified copy of the certificate in Form G on payment of a fee of twenty five rupees.

163.	Fees for inspection and comparison. – (1) The fee for each inspection of the Test Apparatus shall be as follows:-

Rs.

Able Flash Point Apparatus or Pensky-martens Apparatus			200

Barometer											50

Thermometer										50

164.	Fees for testing. – (1) The fee for testing each sample of imported petroleum shall be one hundred rupees:

Provided that the aggregate fee chargeable under this sub-rule shall not, in the case of any one ship, exceed Rs. 1000.

(2)	The fee for re-testing each sample under section 20 of the Act shall be one hundred. It shall be refunded if the original test is proved to be erroneous.

CHAPTER X

Exemption

165.	Power to exempt. – The Central Government may on the recommendation of the Chief Inspector of Explosives in exceptional cases, by order, grant to any person or persons exemption from all or any of the provisions of these rules or such conditions, if any, as may be specified in the order.

==============================

SCHEDULE 1

LICENCES (vide Rule 115)

| Article No. | Form of License (See Schedule (II) | Purpose for which granted | Authority empowered To grant license | Fee |  |
| --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) |  |
| 1 | H | To import dangerous petroleum other than petroleum which can be used in an internal combustion engine, in quantity not exceeding 60 gallons at any one time? | The District Authority | Re. 25. |  |
| 2 | I | To store dangerous petroleum in quantity not exceeding 60 gallons. | The District Authority | Rs. 25. |  |
| 3 4 5 6 7 | J K L M Special Forms | To store non-dangerous petroleum otherwise than in bulk, in quantity not exceeding 5,000 gallons. To store petroleum in a tank or tanks in connection with a pump outfit for fuelling motor conveyances. To import dangerous petroleum and to store petroleum in installations. To import and store dangerous petroleum otherwise than in bulk and to store otherwise than in bulk 9a) non-dangerous petroleum in quantity exceeding 5,000 gallons or (b) partly dangerous petroleum and partly non-dangerous petroleum. To import dangerous petroleum and to store petroleum (in cases not provided for in Articles 1, 2, 3, 4, 5, and 6.) | The District Authority The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector The Chief Inspector or an Inspector of Explosives authorized by the Chief Inspector of Explosives in this behalf. The Chief Inspector | FOR ARTICLES 3, 4, 5, 6 AND 7. Dangerous, Non-dangerous and Heavy Petroleum. |  |
|  |  |  |  | (a) When the quantity to Rs. 60. be stored does not exceed two thousand liters (b) When the quantity to be stored exceeds two thousand liters but does not exceed four thousand liters. (c) When the quantity to be stored exceeds four thousand liters but does not exceed twenty thousand liters (d) When the quantity to be stored exceeds twenty thousand liters but does not exceed two hundred thousand liters. (e) When the quantity to be stored exceeds two hundred thousand liters. | Rs. 60. Rs. 100. Rs. 100 for the first 4000 liters plus Rs. 25 for every additional 4000 liters or part thereof. Rs. 200 for the first 20000 liters plus Rs. 25 for every additional 4000 liters or part thereof. Rs. 1325 for the first 200,000 liters plus Rs. 100, for every additional 100,000 liters or part thereof to a maximum of Rs. 5000 for each category of petroleum |

SCHEDULE II

FORMS

FORM ‘A’

[See Rule 8]

Declaration to be made by the master of a ship carrying before entering a port or by the ship’s agent.

Name of ship ______________

Particulars of the carriage

| Name of Petroleum | Total quantity carried in the ship. | Quantity of petroleum to be landed in - name of port. | Remarks |
| --- | --- | --- | --- |
| Dangerous petroleum which can be used in an internal combustion engine. |  |  |  |
| Other than dangerous petroleum |  |  |  |
| Petroleum certified in accordance with rule 11 other than heavy petroleum |  |  |  |
| Heavy petroleum |  |  |  |
| Other than non-dangerous petroleum |  |  |  |
| Total |  |  |  |

Signature of Master/agent of the ship

Dated

-----------------------------------------

FORM ‘B’

[See Rule 11]

CERTIFICATE OF IMPORTED PETROLEUM

Certified that Sample/Samples of petroleum of the description given below for shipment per S.S. ……………………….to………………………… has/have been tested by me and that its/their flashing point/points as stated against the same.

| Description of petroleum whether in cases, casks, drums, tanks or in bulk | Brand | No of cases, casks, drums or tanks | Quantity | Flashing point |
| --- | --- | --- | --- | --- |

Port of shipment…………………….Name of shipper…………………………………..

Dated the                 day of                     20….

Signature and designation of Testing Officer

##### FORM ‘C’

[See Rule 13]

CERTIFICATE OF STORAGE ACCOMMODATION

I hereby declare that I propose to store the following consignments of dangerous/non dangerous petroleum ex S.S. __________________ arriving in __________________ on or about the _____________________20 ____ at the storage tanks or sheds of with particulars are given in column 1 and 2 of the statement below and 1 certify that the capacity shown as available in column 3 of that statements is available for the storage of the said petroleum and that the said storage tanks and sheds are duly licensed for the storage of the petroleum in question.

Dated the ___________20____

Importer or Agent

##### STATEMENT

| 1 | 2 | 3 | 4 |
| --- | --- | --- | --- |
| Storage tanks or sheds | Total capacity of each storage tank or shed | Capacity available in each storage tank or shed | Capacity to be utilized by present consignment in each storage tank or shed |
|  | Gallons [liters] | Gallons [liters] | Gallons [liters] |
| Total Gallons [liters] |  |  |  |

##### FORM ‘D’

[See Rules 114(2)]

Application for the grant/amendments/renewal/transfer of license to import and store petroleum.

The replies to be given in this Column

1. Particulars of Applicant

Name                                                           …………… …………………………

NIC No.                                                       ……………………………………….

Full Postal Address                                     ………………………………………

……………………………………….

Telephone/FAX/E mail                              ……………………………………….

2. Situation of the premises where

petroleum is to be stored

Province                                                      ………………………………………

District                                                        ………………………………………

Town and village                                        ………………………………………

3. Petroleum proposed to be stored:

(i) Dangerous petroleum

(a) In bulk                                             …………… …………………………

(b) Not in bulk                                      …………… …………………………

(c) Total                                                …………… …………………………

(ii) Heavy petroleum

(a) In bulk                                             …………… …………………………

(b) Not in bulk                                      …………… …………………………

(c) Total                                                …………… …………………………

(iii) Non-dangerous petroleum

(a) In bulk                                             …………… …………………………

(b) Not in bulk                                      …………… …………………………

(c) Total

(iv) Excluded Petroleum

(a) In bulk                                             …………… …………………………

(b) Not in bulk                                      …………… …………………………

(c) Total                                                ……………………………………….

Total [(i) + (ii) + (iii) + (iv)]                         ………………………………………

4. Form in which license is required                   ……………………………………….

5. Do the premises fulfill all the conditions endorsed on the form? ……………………

6. Petroleum already stored in the premises:

(i) Dangerous petroleum                             …………… …………………………

(a) In bulk                                              …………… …………………………

(b) Not in bulk                                       …………… …………………………

(c) Total                                                 …………… …………………………

(ii) Heavy petroleum                                   …………… …………………………

(a) In bulk                                              …………… …………………………

(b) Not in bulk                                       …………… …………………………

(c) Total                                                 …………… …………………………

(iii) Non-dangerous petroleum

(a) In bulk                                              …………… …………………………

(b) Not in bulk                                       …………… …………………………

(c) Total                                                 …………… …………………………

(iv) Excluded Petroleum

(a) In bulk                                              …………… …………………………

(b) Not in bulk                                       …………… …………………………

(c) Total                                                 …………… …………………………

Total [(i) + (ii) + (iii) + (iv)]                                ………………………………………

7. Dangerous petroleum proposed to be imported.

(a) In bulk                                             …………… …………………………

(b) Not in bulk                                      …………… …………………………

(c) Total                                                …………… …………………………

I hereby declare that the statements made above have been checked up by me and are true and I undertake to abide by the terms and conditions of the license which will be granted to me.

Date of application   ……………

Signature and designation of the applicant.

Notes.

1. Where the application is made on behalf of a company, the name and address of the company and the name of the manager or agent should be given and the application should be signed by him. Every change in the name of the manager or agent shall be forthwith intimated to, and his specimen signature filed with, the licensing authority.

2. “In bulk” means in tanks or receptacles exceeding 1,000 liters in capacity “Not in bulk” means in approved containers not exceeding 1,000 liters in capacity.

3. (i)  This application, if it relates to a new installation or storage shed or fueling station or if the applicant proposes any alterations in an existing installation or storage shed or fueling station, must be accompanied by specifications and four copies of plans drawn to scale. The plan should clearly indicate;-

(a)  the manner in which the conditions prescribed by these rules have been complied with;

(b)  the premises to be licensed, the area of which shall be distinctively colored or otherwise defined;

(c)  the surroundings and all protected work;

(d)  the position and capacity of all storage tanks/cylinders, storage and filling sheds, dispensers and the   position of all other facilities, buildings and erections forming part of the installation/fueling station;

(e)  the area reserved for all kinds of petroleum

(f)  tanks and other enclosures; and

(g)  all pumps, valves, fittings, filling and discharge points, vent pipes etc.

(ii)  License together with approved plan and specifications attached there to. (Not required for the first   grant of license)

(iii)  “No Objection Certificate” from the District Authority. (Not required for renewal, transfer and amendment of a license without any change in the site of the licensed premises).

(iv) Requisite amount of fees.

(v)  A certificate of tank testing if required.

(vi) A certificate of safety if required.

--------------------------------------------------

FORM ‘D-1’

[See Rule 77]

Application for grant/renewal of license to transport petroleum in bulk on land by mechanically propelled vehicles.

Replies to be given in this column.

1. Particulars of Applicant

Name                                                           …………… …………………………

NIC No.                                                       ……………………………………….

Full Postal Address                                     ……………………………………….

………………………………………..

Telephone/FAX/E mail                              ………………………………………..

2.	Description of the vehicle

(a)	Make and model		        ……………………………………

(b)	Engine number		        ……………………………………

(c)	Chassis number		        ……………………………………

(d)	Registration number		        ……………………………………

(e)	Name and the registration owner    ……………………………………

(f)	Total number of compartments       ……………………………………

(g)	Capacity of each compartment        ……………………………………

in kilo liter

(h)	Class(es) of petroleum authorized

to be carried in the vehicle               …………………………………

I hereby declare that the statements made above have been checked up by me and are correct to the best knowledge and I undertake to abide by the terms and conditions of the license which will be granted to me.

Date of application 						Signature of the applicant

Where the application is made on behalf of the company, the name and address of the company and the manager or agent should be given and the application should be signed by him. Every change in the name of manager or agent shall be forthwith intimated to and his specimen signature filed with the licensing authority.

FORM ‘E’

[See Rule 158 (3)]

Certificate of Apparatus

.........................................................................................................................Appartus

Marked No....................................................................................................................

Maker's Name...............................................................................................................

Slide No.........................................................................................................................

Thermometer No. ...........................................Oil Cup No.............................................

Water Bath Cup No........................................................................................................

The above apparatus including the thermometers having been submitted for verification with the Standard Test Apparatus was compared by me on and found to agree with it within the prescribed limits.

The following corrections are necessary to the thermometer and barometer or aneroid readings:

Thermometer No................................................................................................................

No.................................................................................................................

Barometer or aneroid No....................................................................................................

This certificate is valid for a period of three years from

Date.............................

Reference.............................

Signature and designation of the Officer 
(Appointed under Sec. 15(1) of the Petroleum Act, 1934.)

##### FORM ‘F’

##### [See rules 159]

Register of Certificate Apparatus

| Serial No. | Place at which the apparatus is intended to be used | Number and date engraved on the apparatus | Contents of Certificate | Date of which certificates will cease to be valid. |
| --- | --- | --- | --- | --- |

FORM ‘G’

[See Rule 162]

Certificate of tests of petroleum

Owner.............................................................................................................................

Marks.............................................................................................................................

Test

- ............................................................................................................................

- ............................................................................................................................

- ............................................................................................................................

Average ................................................................................................Thermometer

Correction................................................................................................................

The sample is............................................................................................................

Petroleum and (in the case of Non-dangerous petroleum) has a flash point of...............................................................................................................................

Place..............................

Date..............................                                                                        Testing Officer

-----------------------------------

FORM ‘H’

[Article 1 of Schedule I]

License to import dangerous petroleum other than petroleum which can be used in an internal combustion engine, in quantity not exceeding 60 gallons [300 liters]

No……………………..	 					Rs………………

License is hereby granted to …………………………………………..to import dangerous petroleum other than petroleum which can be used in an internal combustion engine, not exceeding 300 liters in quantity at any one time, at the Port of…………….. subject to the provisions of the petroleum Act, 1934 and the rules made there under and to further conditions on the back of this license.

This license shall remain in force till the …………… 20 ………………

The …………………20……………

District Authority

CONDITIONS OF LICENSE

1.	Dangerous petroleum shall be imported in gas-light timed, galvanized or otherwise externally rust-proof sheet iron or steel receptacles which shall fitted with well made apertures and well-fitting screw plugs or with screw caps or other caps with metal air-tight under caps.

2.	The receptacles shall have the following thickness of metal;

Capacity exclusive of the prescribed air space -                          Not less than –

Not exceeding 2 gallons					                    0.443mm (27 BG)

Exceeding 2 but not exceeding 4 gallons	                                0.63mm	(24 BG)

Exceeding 4 but not exceeding 30 gallons	                    0.80mm	(22 BG)

Exceeding 30 but not exceeding 45 gallons	                    1.25mm	(18 BG)

Exceeding 45 gallons	                                                        1.59mm	(16 BG)

3.	The receptacles shall be so constructed and secured, as not be liable, except under circumstances of gross negligence or extra-ordinary accident, to become defective, leaky or insecure in transit and shall bear a stamped, embossed, pointed or printed warning exhibiting in conspicuous characters the words ‘Highly Inflammable’ or an equivalent warning of the dangerous nature of the petroleum.

4.	An air space of not less than 5 percent of its capacity shall be left in each receptacle at the time of filling.

## FORM ‘I’

[Article 2 of Schedule I]

License to store dangerous petroleum in quantity not exceeding 60 gallons [300 liters].

No. ……………….. 							Fee Rs…………….

License is hereby granted to ……………………………………………………… valid only for the storage of …………… gallons of dangerous petroleum in the storage shed described below, subject to the provisions of the petroleum Act, 1934 and the rules made there under and to the further conditions on back of this license.

This license shall remain in force till the 31st day of December.

The…………………. 19 ……………

District Authority

Description of the storage shed referred to above

…………………………………………………………………………………………..

………………………………………………………………………………………….

| Date of renewal | Date of expiry | Signature licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed premises are not found conforming to the description and condition attached hereto and contravention of any of the rules and conditions under which this license is granted is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

CONDITIONS

1. Dangerous petroleum shall be stored only--
(i) in a storage shed constructed of suitable non-combustible materials on private ground; the doors and windows may be of wood; or 
(ii) in a properly ventilated iron bin of a design approved by the Chief Inspector and placed on private ground in the open air.

2.  The storage shed shall be adequately ventilated near the ground level and also near the roof. The ventilators shall be provided with two layers of non-corroding metal wire gauze having not less than 28 to the linear inch [11 meshes per linear centimeter].

3…The storage shed shall not form part, or be attached to any building in which any person resides or works or where person assemble for any purpose unless it is separated there from by a substantial roof and partition wall of masonry construction having no openings therein.

- The storage shed if in any building, shall not be situated under any staircase or under any other means of exit likely to be required to be used for escape in case of fire.

- Any two storage sheds or bins or other storage premises not more than twenty feet [six meters] apart shall be deemed to be one storage shed.

- No alterations shall be carried out in the storage shed or bin without the previous sanction in writing of the licensing authority.

- If the licensing authority calls upon the holder of a license, by a notice in writing to execute any repairs to the storage shed, which are, in the opinion of such authority necessary for the safety of the shed, the holder of the license shall execute the repairs within such period as may be fixed by the notice.

- All empty receptacles which have contained dangerous petroleum shall except when they are opened for the purpose of cleaning them and rendering them free from petroleum vapour be kept securely closed unless they have been thoroughly cleaned and freed from petroleum vapour.

- No receptacles shall be repaired on the premises and no person shall repair or cause to be repaired any receptacle in which to his knowledge, any dangerous petroleum is or has been kept until he has taken all reasonable precautions to ensure that the receptacle has been rendered free from such petroleum and any inflammable vapour.

- Adequate precautions shall be taken at all times for the prevention of accident by fire or explosion.

- Every care shall be taken to prevent any dangerous petroleum escaping into any drain, sewer, harbour, river or watercourse.

- Adequate precautions shall be taken to prevent unauthorized persons having access to any dangerous petroleum kept and to the vessel which contains or has contained such petroleum.

- The licensee shall keep daily records and accounts of all receipts and issues of petroleum in such form as the licensing authority may from time to time prescribe and shall exhibit his stock and records to an Inspector or sampling officer on demand.

- Any accident by fire or explosion occurring within the licensed premises, which is attended with loss of human life or serious injury to person or property shall be reported to the nearest Magistrate or to the officer-in-charge of the nearest police station and to the Chief Inspector of Explosives immediately and by telegraph or telephone where such means of communication are available.

- Free access to the licensed premises shall be given at all reasonable times to any inspector or sampling officer and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed

----------------------------

##### FORM ‘J’

[Article 3 of Schedule I]

LICENSE TO STORE NON-DANGEROUS PETROLEUM, OTHERWISE

THAN IN BULK IN QUANTITY NOT EXCEEDING 5000 GALLONS.

No. ……………	 						Fee Rs……………

License is hereby granted to ……………………………………….. valid only for the storage of …………………gallons of non-dangerous petroleum in the storage shed

described below, subject to the provisions of the petroleum Act, 1934, and the rules made there under and to the further conditions on the back of this license.

This license shall remain in force till the 31st day of December 19………

The …………………19…………

The District Authority

Description and location of the storage shed referred to above.

| Date of renewal | Date of expiry | Signature licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the license premises, when inspected, are not found conforming to the description and condition attached hereto and contravention of any of the rules and condition under which this license is granted is also punishable with fine which may extend to five hundred rupees for the first offence and which may extend to two thousand rupees for any subsequent offence.

--------------------------------

CONDITIONS OF LICENSE

- The petroleum shall be stored only in the storage shed, which shall be constructed of suitable uninflammable materials, but the beams, rafters, column, windows and doors may be of wood. The building shall rest on foundation walls the walls and floors being suitably finished to form a sump or enclosure not more than 60 centimeters in depth and capable of receiving and retaining, in cases of accident to emergency, a volume not less than the maximum quantity of petroleum allowed in the building.

- The storage shed shall not form part of, or be attached to any building in which any person resides or works or where persons assemble for any purpose unless it is separated there from by a substantial floor or partition which is constructed or uninflammable material and has no opening in it.

- The storage shed, if in any building, shall not be situated under any staircase or under any other means of exit likely to be required to be used for escape in case of fire.

- No alterations shall be carried out in the storage shed without the previous sanction in writing of the licensing authority.

- If the licensing authority calls upon the holder of a license, by a notice in writing to execute any repairs to the storage shed, which may in the opinion of such authority, be necessary for the safety of the shed, the holder of the license shall execute the repairs within such period, not being less than one month from the date of receipt of the notice, as may be fixed by the notice.

- Any two storage sheds not more than 4.5 meters apart shall be deemed to be one storage shed.

- Non-dangerous petroleum shall be packed in airtight tins or drums of steel or iron in other receptacle not easily broken.

- The drum or other receptacle containing petroleum shall only be opened in the licensed premises and for the time necessary for drawing off the petroleum and during such drawing off every reasonable precaution shall be adopted for preventing the escape of petroleum or the vapor there from.

- Adequate precautions shall be taken to prevent unauthorized persons having access to any petroleum kept and to any receptacles, which contain or have contained petroleum.

- Adequate precautions shall be taken all the time for the prevention of accident by fire or explosion.

- Every care shall be taken to prevent any petroleum escaping into any drain, sewer, harbor, river or watercourse.

- The licensee shall keep daily accounts and records of all the receipts and issue of petroleum in such form as the licensing authority may, from time to time, prescribe and shall exhibit his stock and records to an Inspector or Sampling officer on demand.

- Any accident, fire or explosion occurring within the licensed premises causing loss of human life or serious injury to person or property, shall be reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station and to the Chief Inspector of Explosives, Karachi, immediately and by telegraph, fax or telephone where such means of communication are available.

- Free access to the licensed premises shall be given at all reasonable times to any Inspector or Sampling Officer and every facility shall be afforded to such officer ascertaining that the rules and conditions of this license are duly observed.

---------------------------

FORM ‘K’

(Article 4 of Schedule I)

License to store petroleum in a tank

or tanks in Connection with a pump outfit for fuelling motor vehicles.

No……………..					               License Fee Rs………….

License is hereby granted to _________________________________________

_______________________________________________________________valid only for the    storage of under mentioned facilities/kinds and quantities of petroleum in underground tank (tanks) in the licensed premises described below and as shown on the plan hereto attached subject to the provisions of the Petroleum Act, 1934, and the rules made thereunder and to the further conditions or of the rules framed there under or of any condition of this license.

This license shall remain in force till the 31st day of December ________.

This license is liable to be cancelled if the licensed premises when inspected are not found conforming to the description and conditions attached hereto and contravention of any of the rules and conditions under which this license is granted is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

Dated the _____ day of ______, _______. 				Licensing Authority

Plan No………………………………  dated……………………..

Description of the licensed premises referred to above.

The licensed premises is situated at __________________________________

_________________________________________________________________and consist of gas-tight tank (tanks) and other facilities as per detail(s) given below:

| Petroleum Facility (ies) allowed at the licensed premises |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl.No. |  | Tank Number | Kind of Petroleum |  | Quantity in Liters | Fee in Rupees |
| (i) |  |  |  |  |  |  |
| (ii) |  |  |  |  |  |  |
| (iii) |  |  |  |  |  |  |
| (iv) |  |  |  |  |  |  |
| (v) |  |  |  |  |  |  |
| (vi) |  |  |  |  |  |  |
| (vii) |  |  |  |  |  |  |
| Ancillary Facility (ies) allowed at the licensed premises |  |  |  |  |  |  |
|  |  | Name of Facility |  | Dimensions | Date of approval |  |
| (a) |  |  |  |  |  |  |
| (b) |  |  |  |  |  |  |
| (c) |  |  |  |  |  |  |
| (d) |  |  |  |  |  |  |
| (e) |  |  |  |  |  |  |
| Total License Fee |  |  |  |  |  |  |

Space for endorsement of Renewals:

| Date of Renewal | Date of Expiry | Signature of Licensing Authority |
| --- | --- | --- |

CONDITIONS OF LICENCE

1.	The petroleum shall be stored in one or more gas-tight metal tanks of a capacity (ies) mentioned above sunk completely underground in the position shown on the plan attached hereto and each placed in a masonry or concrete pit, the tank being packed round with sand, earth or clay so that no air-space is left between the tank and the masonry or concrete pit and the tank is not visible. Such masonry or concrete pit shall not be obligatory if the rank is a welded one tested up to a pressure of 3 lbs. per square inch and is buried and is on private, leased or rented land away from public traffic. The space over the buried tanks must not be used for any purpose.

2.	There shall be no openings in any tank other than those necessary for the introduction or removal of the petroleum or for ventilating or dipping the tank. The filling and dipping pipes shall be carried down nearly to the bottom of the tank.

3.	Every tank shall be fitted with a vent pipe leading into the open air. The vent pipe shall be securely supported and shall be not less than 12 feet in height. The upper opening shall be covered with fine copper or other non-corroding metal wire gauze of mesh not less than 28 to the linear inch and fitted with a hood or the upper opening shall be fitted with an inlet valve and an exhaust valve.

4.	After the 1st April 1937, no pump or tank shall be erected inside a building and, if prior to that date any tank is installed inside a building, it shall only be filled from a tank-wagon through an underground filling pipe having a filling point in the open air at a distance of not less than 12 feet from the building.

5.	No alteration of the premises including the position of a pump or tank and no replacement of a tank shall be effected except with the previous sanction in writing of the licensing authority. All alterations sanctioned under this condition shall be shown on an amended plan to be attached to this license.

6.	If the licensing authority calls upon the holder of a license by a notice in writing to execute any repairs to the licensed premises which are, in the opinion of such authority, necessary for the safety of the premises, the holder of the license shall execute the repairs within such period, not being less than one month from the date of receipt of the notice, as may be fixed by the notice.

7.	Every tank, before being repaired, shall be cleared of all petroleum and of all inflammable vapours. When a tank in position is open for cleaning or repairs no electric or other lamps, electric cables or electric fans shall be brought near the manhole of the tank until the tank has been certified in writing to be “gas free” by a qualified Chemist or Engineer. (The inside of the tank may be lighted by the use of mirrors.)

8.	The petroleum shall enter a tank “under seal” and shall not be” supplied to the tank between the hours of sunset and sunrise except by) a motor tank-wagon of a type approved by the Chief Inspector for the purpose and with the approval in writing of the licensing authority.

Note:	A pipe supplying liquid to a tank is “under seal” to that tank if it is screwed to the tank or otherwise attached so that no liquid or vapour can escape into the air except through the vent pipe fitted to the tank as required by condition 3.

9.   No artificial light capable of igniting inflammable vapour shall at any time be present in the immediate vicinity of the tank-wagon during the transfer of the petroleum to the tank and no person engaged in such transfer shall smoke. When the underground tank is filled with petroleum from barrels no such light shall be allowed within a distance of 30 feet from the barrels.

10.	No petroleum shall be removed from a tank except by means of the pump or pumps at the position marked on the plan hereto attached. Every pump shall together with its connections and fittings be so constructed and maintained as to be gas and petroleum-tight. The pipe connections between the tank and a pump shall be placed underground.

- For the purpose of charging the tanks of motor vehicles the petroleum shall only be supplied by being.

- pumped through strong metal piping by means of approved pumps into above ground measuring tanks of a capacity not exceeding 30 gallons, fixed in approved positions, and run thence through sound house, fitted with a secure self-closing cock and nozzle, into the tanks of motor vehicles, or

- pumped through strong metal piping by means of approved pumps into an above ground service tank of approved capacity, fixed in an approved position, and run thence through strong  metal piping into measuring tanks of a capacity not exceeding 30 gallons fixed in approved position  and thence through sound hose, fitted with a secure self closing cock and nozzle into the tanks of motor vehicles, or

- pumped by means of approved measuring pumps, fixed in approved positions, through sound hose fitted with a secure tap and nozzle, into the tanks of motor vehicles.

12.	Petroleum may be supplied to a motor vehicle between the hours of sunset and sunrise from the pump provided that (i) lights other than the electric lights of the vehicle receiving the petroleum are extinguished, (ii) the pump and the vehicle are illuminated by electric light or failing this by some other form of lighting and (iii) no light capable of igniting inflammable vapour is situated or brought within twelve feet of the pump or vehicle receiving the petroleum.

13.	(a) 	Petroleum shall not be placed in any motor vehicle while the engine is running and, where the vehicle is licensed for the conveyance of more than six passengers on hire, while any passenger remains in the vehicle, and

(b) 	Persons in and engaged in connection with any motor vehicle shall not be permitted to smoke while it is being refueled.

14.	Except when absolutely necessary for the purposes of condition 7 or for testing the accuracy of the pump’s discharge by means of a standard capacity measure, petroleum shall not be filled from the tank or pump into any receptacle other than the fuel tank of a motor vehicle.

15.	This license shall be held to cover the use of a portable kerb-side pump outfit for a period of not more than one month in the place of the licensed permanent outfit in the event of the latter being out of order, provided notice in writing is given to the licensing authority before the portable pump is taken into use, and the conditions of this license which apply to a portable pump are observed. No petroleum shall be allowed above ground (except that actually in the pump) in any case where the underground tanks can be used in connection with the portable pump by making a temporary connection from the portable pump to the underground tank.

16.	In cases where portable pumps, are used not more than two barrels of petroleum in reserve shall be kept within 20 feet of the pump or on public property nearby.

17.	A licensee who stores dangerous petroleum intended for sale may stock in a building within the licensed premises not more than 6 gallons of dangerous petroleum in securely closed two-gallon standard tins, and shall, if so required by the District Authority, stock at least 2 gallons.

18.   Adequate precautions shall be taken to prevent unauthorized persons from having access to the petroleum or to the vessels, which contain or have contained petroleum.

19.	Every person managing or employed on or in connection with the licensed premises shall abstain from any act whatever which tends to cause fire or explosion and which is not reasonably necessary and to the best of his ability, shall prevent any other person from doing such act.

20.	Every care shall be taken to prevent any petroleum escaping into any drain or sewer.

21.	The licensee shall provide for each pump, whether curbside or portable, a minimum of two tins or drums of dry sand which shall be kept ready for extinguishing fires.

22.	Any accident, fire or explosion occurring within the licensed premises, which is attended with loss of human life or serious injury to person or property, shall be reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station immediately and by telegraph or telephone where such means of communication are available.

23.	Free access to the licensed premises shall be given at all reasonable times to any Inspector or sampling Officer and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed.

24.	Electrically operated pumps must comply with the following conditions, namely:-

- the motor, switch gear an all wiring on the pump casing shall be of flame proof construction satisfying the requirements of B.S.S. No. 229, and

- a double poled switch shall be provide in an immediately accessible position not less than 12 feet from the pump and must be so connected as to be capable of completely isolating the pump from the electric supply

- (a) The licensee shall keep records and accounts of all petroleum in stock and of sales or issues thereof. The accounts shall clearly indicate date-wise the opening balance, receipts, sales, closing balance and meter numbers. Separate account shall be maintained for efferent categories of petroleum.

(b) The licensee shall exhibit his stock book and records to any officer authorized under section 13 of the Petroleum Act, 1934, whenever such an officer calls upon him to do so.

- Before petroleum is stored in the premises, the licensee shall send to the licensing authority a report in writing to the effect that the premises have been built according to the approved plan.

| Nature of amendments | Date | Signature of licensing authority |
| --- | --- | --- |
| 1. Dealer’s name |  |  |
| 2. Trade name |  |  |

Further condition(s) of the license:

Signature/Stamp of the Authority

-----------------------------

FORM ‘L’

[Article 5 of Schedule I]

License to import dangerous petroleum and to store petroleum in installations

No.	…………………							Fee Rs……………………

License is hereby granted to……………………………………………valid only for	 the importation of …………………gallons of dangerous petroleum and for the storage of ……………………………………………………gallons of petroleum in the place described below and shown on the plan attached hereto subject to the provisions of the petroleum Act, 1934 and the rules made there under and to the further condition on the back of this license.

This license shall remain in force till the 31st day or December 19 …………

| Sl.No. | Nature of Petroleum to be stored/imported | Quantity of petroleum (In gallons) |
| --- | --- | --- |
|  | Dangerous petroleum in bulk |  |
|  | Dangerous petroleum not in bulk |  |
|  | Heavy petroleum in bulk |  |
|  | Heavy petroleum not in bulk |  |
|  | Non-dangerous petroleum in bulk |  |
|  | Non-dangerous petroleum not in bulk |  |
|  | Excluded petroleum in bulk |  |
|  | Excluded petroleum not in bulk |  |
|  | Total |  |

Chief Inspector of Explosives

Plan No. …………………………dated …………

Description of the place referred to above …………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………..

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

GENERAL CONDITION

This license is liable to be cancelled if the licensed premises, when inspected, are not found conforming in the description and conditions attached hereto and contravention of any of the rules and conditions under which this is granted is also punishable with fine may extend to five hundred rupees for a first offence and may extend to two thousand rupees for any subsequent offence.

CONDITIONS OF LICENSE

- Petroleum shall be kept only in the storage tanks and storage and filling sheds or other approved places within the installation specified for the purpose on the plan attached hereto.

2.	(i) 	The tank or tanks shall be supported on   an approved foundation and shall be surrounded by a wall or embankment of substantial construction, or shall be partially sunk in as excavation. The enclosure thus formed shall contain only one of the following classes of petroleum, shall be of dimension sufficient to contain the quantity of petroleum specified under the class to be stored and shall be so constructed and maintained as to the escape there from of any petroleum in the form of liquid whether under the action of fire or otherwise;

- Dangerous petroleum … 10 percent more petroleum than the tank or tanks are capable of containing;

- Non-dangerous petroleum other than class C petroleum … the amount of petroleum the tank or tanks are capable of containing;

- Heavy petroleum … the amount of petroleum the largest tank in the enclosure is capable of containing;

Provided that heavy petroleum may be stored in the same enclosure as non-dangerous petroleum other than heavy petroleum if the dimension under (b) above is observed.

(ii) 	Except for the necessary pipes and valves the space within an enclosure and not occupied by the tank or tanks, shall be kept entirely clear and unoccupied. Alternatively gas-tight metal tanks may be sunk completely underground the tanks being packed round with sand, earth or clay, so that no sir space is left below ground level and tank is not visible. Tanks so buried shall not be required to maintain the safety distance laid down in condition 8 but the space over the buried tanks must not be used for any purpose. The filling and dipping pipes in an under ground tank shall be carried down to the bottom of the tank.

(3)	All tanks shall be fitted with a vent pipe leading into the open air, the open end being covered with fine copper or other non-corroding metal wire gauze of mesh not less than 28 to the linear inch [11 per linear centimeters] and fitted with a hood or the tank shall be fitted with an approved relief valve or other approved means for preventing dangerous internal or external pressures being produced.

(4)	Cast iron valves are not permitted on any tank and all valves in an installation must be permanently marked in a manner clearly indicating the direction of opening and shutting the valves.

(5)	Pumps shall be placed only in position shown on the plan attached hereto and they shall together with all connections and fittings be so constructed and maintained as to prevent leakage of petroleum.

(6)	Storage or filling sheds shall be constructed of suitable un-inflammable material. The building shall rest on foundation walls and shall be surrounded by a wall or embankment of substantial construction or the walls and floor shall be suitably finished to form a sump or enclosure not more than two feet deep. A combination of these methods is permissible. The enclosure or sump thus formed shall be of sufficient capacity to contain the total quantity of petroleum liable at any time to be present in the building and shall be so constructed and maintained as to prevent the escape there from of any petroleum in the form of liquid whether under the action of fire or otherwise. In the case of dangerous petroleum or partly dangerous petroleum the enclosure or sump shall be capable of receiving and retaining a volume not less than 5 percent in excess of the maximum quantity allowed in the building. The sumps and enclosures must be kept clean and free from any accumulation of inflammable liquids.

(7)	Every storage or filling shed in which dangerous petroleum is stored or filled shall be adequately ventilated near the ground level immediately above any walls constructed to prevent any leakage of petroleum and also near or in the roof.

The ventilators shall be provided with two thickness of fine copper or other non-corroding metal wire mesh of not less than 28 to the linear inch [11 per linear centimeters].

(8)	(a) 	A distance of not less than 100 feet shall be kept clear between;

- A storage tank and any other storage tank;

- Between storage tank and storage or filling shed, the distance being measured between the nearest points of the perimeters of the storage tanks or storage or filling sheds, as the case may be.

(b) 	A distance of not less than 150 feet shall be kept clear between any storage tank or storage or filling shed and nay protected work.

(c)	Notwithstanding anything contained in clause (a) or clause (b) -

(i)	Where the quantity of dangerous petroleum or partly dangerous and partly non- dangerous petroleum not in bulk to be stored in a storage shed does not exceed 50,000 gallons, the following reduced distance may be kept clear between the shed or enclosure wall and (A) any other building forming part of the installation, (B) any protected work, or (C) any storage tank containing non-dangerous petroleum having a capacity not exceeding 50,000 gallons:-

Not exceeding 1,000 gallons                                                           20 feet

Exceeding 1,000 gallons but not exceeding 10,000 gallons	         30 feet

Exceeding 10,000 gallons but not exceeding 20,000 gallons	         40 feet

Exceeding 20,000 gallons but not exceeding 30,000 gallons	         50 feet

Exceeding 30,000 gallons but not exceeding 40,000 gallons           60 feet

Exceeding 40,000 gallons but not exceeding 50,000gallons           70 feet

(ii)	When a storage tank containing non-dangerous petroleum has a capacity not exceeding 100,000 gallons, a distance of not less than 50 feet may be kept clear between it and (A) another such tank of similar or less capacity or (B) a storage or filling shed containing non-dangerous petroleum. Such a storage tank and storage or filling shed may, where the total quantity stored does not exceed 200,000 gallons. Keep a distance of not less than 50 feet clear between the enclosure walls or embankment and any protected works;

- When a storage tank containing non-dangerous petroleum has a capacity not exceeding 50,000 gallons, distance of –

  - For horizontal tanks, not less than one third; and

  - For perpendicular tanks, not less than one-half of the height of the tank may be kept clear between it and (A) another such tank or (B) a storage or filling shed wherein non-dangerous petroleum is stored in quantity not exceeding 50,000 gallons. Such a storage tank and stores or filling shed may, where the total quantity stored does not exceed 100,000 gallons keep a distance of lot less than 20 feet clear between the enclosure wall or embankment and any protected works.

- In case of heavy petroleum a distance of not less than 20 feet may be kept clear between a storage tank and (A) another such tank or (B) a storage of filling shed containing such petroleum and a distance of not less than 50 feet shall be kept clear between such storage tank or filling or storage shed and any protected work.

When the total quantity stored in such storage tank and storage and filling shed does not exceed 100,000 gallons half the distance given in clause (iii) for the like quantity of non-dangerous petroleum other than heavy petroleum may be observed.

9.	The distance specified in condition 8 may be reduced by the licensing authority in cases where screen walls are provided or other special precautions are taken or where there are special circumstances that, in his opinion warrant the alteration.

10.	Notwithstanding anything herein to the contrary when petroleum is stored in an installation at or near wells, pumping stations or refineries, the concessions in clause (C) of condition 8 shall not apply and no storage tank, the capacity of which exceeds 50,000 gallons, or storage or filling shed shall be placed nearer than 300 feet to any still, boiler, furnace or fire. In such as installation all tanks shall be situated in a compact area;

- Under a single control,

- Enclosed or capable or being enclosed by one continuous fence,

- On which there shall be no protected works.

11.	No alteration shall be carried out in the installation without the previous sanction in writing of the licensing authority. Such alteration so sanctioned shall be shown on an amended plan to be attached to this license.

12.	If the licensing authority calls upon the holder of a license, by a notice in writing to execute any repairs to the licensed premises which are in the opinion of such authority necessary for the safety of the premises, the holder of the license shall execute the repairs within such period, not being less than one month from the date of receipt of the notice, as may be fixed by the notice.

    - The responsible agent or supervisor referred to in rule 92 shall not allow any person to enter a tank, which has contained petroleum, unless –

(a)	Such person wears a safety helmet of a description approved by the Chief Inspector; or

(b)	(i) The  responsible agent  or supervisor has certified in writing as the result of an examination of the tank by himself or by some other competent person that the atmosphere in the tank is fit for person to enter; and

(ii) At least one safety helmet of a pattern approved by the Chief Inspector shall have been kept ready for instant use at the manhole of the tank, which is being cleaned or repaired.

    - No work, involving the use of fire, welding or hot reverting, shall be performed in or on any tank until the tank has been certified in the manner laid down in clause (b) of condition 13 to be free from petroleum vapour. When any water is pumped into or withdrawn from the tank no further work of the above description shall be done until the tank has been rested and a fresh certificate issued. When a tank is open for cleaning or repairs no lamps of any description either ordinary or electric torches, electric cables or fans other than of a flameproof type satisfying the requirements of the British Specification No, 229 shall be brought near the tank.

    - No person shall repair or cause to be prepared any receptacle or pipe in which to his knowledge any petroleum is or has been kept until he has taken all reasonable precautions to ensure that the receptacle or pipe has been rendered free from petroleum and any inflammable vapor.

Provided that this condition shall not be deemed to prohibit the usual soldering operations connected with the filling and dispatching of petroleum receptacles.

    - All empty receptacles which have contained dangerous petroleum shall, except when they are opened for the purpose of cleaning them and rendering them free from petroleum vapour, be kept securely closed unless they have been thoroughly cleaned and freed form petroleum and inflammable vapour.

17.	(a) Adequate    precautions    shall    be   taken at all time for the prevention of accident by fire or explosion.

(b) Wherever so specified by the Chief Inspector storage tank shall be fitted with approved fire foam attachments which shall be maintained in proper orders at all times.

18.	Every care shall be taken to prevent any petroleum escaping into any drain, sewer harbor, river or watercourse and enclosure or sumps must not be permanently connected with any drain or sewer.

19.	Any accident, fire or explosion occurring within the area specified in the license causing loss of human life or serious injury to person or property shall be reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station immediately and by fax, telegraph or telephone where such means of communication are available.

20.	Free access to the licensed premises shall be given at all reasonable times to an Inspector or Sampling Officer and every facility shall be afforded to such officer for ascertaining that the rules are the conditions of this license and duly observed.

21.   (i)  (a) 	All permanent pipelines shall be of metal and shall be constructed according to sound engineering practice and shall have a reserve strength of not less than 50% above the working pressure.

(b) 	Hose pipes and rubber flexible pipes used in connection with loading or unloading of petroleum from an installation or forming part of a piping system shall have reserve strength of at least 33½% above the working pressure.

(ii)	All metal pipes shall be flexible pipes shall be tested once every 6 months by a competent engineer holding license to ascertain fitness and compliance with the requirement of strength laid down above.

(iii)	(a) 	A complete and permanent record of such testing shall be maintained in the licensed premises.

(b) 	The date of the last test shall be recorded on the pipes and pipe sections concerned in a distinctive manner.

22.	The license shall not deliver from the licensed premises:-

  - Petroleum in bulk to any vessel used in the carriage of petroleum in bulk by water; and

  - Any petroleum in bulk shall be delivered to any vehicle used for the transport of petroleum in bulk by road unless such vehicle is licensed by the Chief Inspector

----------------------------

FORM ‘M’

[Article 6 of Schedule I]

License to import and store dangerous petroleum otherwise than in bulk (a) non-dangerous petroleum in quantity exceeding 5000 gallons, or (b) partly dangerous petroleum and partly non- dangerous petroleum.

License No.	……………………..				     Fee Rs…………………

License hereby granted to ………………………………… valid only for the importation of ……………..gallons of dangerous petroleum and for the storage of …………… gallons of dangerous petroleum and …………..gallons of non-dangerous petroleum in the storage shed described bellow and shown on the approved plan attached hereto, subject to the provisions of the petroleum Act, 1934 and the rules made there under and to the further conditions of this license.

The ……………………… 20 ……………

Licensing Authority

DESCRIPTION OF THE LICENSED PREMISES

The licensed premises are situated at………………………………………… ………………………………………………………..and consist of ……………….     ………………………………storage shed(s), other facilities and the adjoining areas shown in the attached approved plan.

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed premises when inspected are not found conforming to the description and conditions attached hereto and contravention any of the rules and conditions, under which this license is granted, is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

CONDITIONS OF LICENSE

1. The petroleum shall be stored only in the storage shed which shall be constructed of suitable non-flammable material provided that, when only non-dangerous petroleum is stored, the beams, ratters, columns, windows and doors may be of wood.

The building shall rest on foundation walls and shall be surrounded by wall or embankment of substantial construction or the walls and floor shall be suitably finished to form a sump of enclosure not more than two feet deep. A combination of these methods is permissible. The enclosure or sump thus formed shall be of sufficient capacity to contain the total quantity of petroleum liable at any time to be present in the building and shall be so constructed and maintained as to prevent the escape therefrom of any petroleum in the form of liquid whether under the action of fire or otherwise. In the case of dangerous petroleum or partly dangerous and partly non-dangerous petroleum the enclosure or sump shall be capable of receiving and retaining a volume not less than 5 per cent in excess of the maximum quantity allowed in the building. The sumps and enclosures must be kept clean and free from any accumulation of inflammable liquids.

2. The storage shed, if it is used for the storage of dangerous petroleum, shall be adequately ventilated near the ground level immediately above any walls constructed to prevent any leakage of petroleum and also near or in the roof. The ventilators shall be provided with two thicknesses of fine copper or other non-corroding metal wire gauze of mesh not less than 28 to the linear inch.

3. If the licensing authority calls upon the holder of a license, by a notice in writing to execute any repairs to the licensed premises which may, in the opinion of such authority, be necessary for the safety of the premises, the holder of the license shall execute the repairs within such period, not being less than one month from the date of receipt of the notice, as may be fixed by the notice.

4. No alteration shall be carried out in the licensed premises without the previous sanction in writing of the licensing authority. All alterations shall be shown on an amended plan to be attached to this license.

5, The following distances shall be kept clear at all times between protected works and a storage shed or an enclosure wall used for the storage of dangerous petroleum or partly dangerous and partly non-dangerous petroleum:-

| Quantity to be stored | Distances to be kept clear feet |
| --- | --- |
| Not exceeding 500 gallons | 20 |
| Exceeding 500 gallons but not exceedmg 1,000 gallons | 25 |
| Exceeding 1,000 gallons but not exceeding 5,000 gallons. | 30 |
| Exceeding 5,000 gallons but not exceeding 20,000 gallons. | 40 |
| Exceeding 20,000 gallons but not exceec1ing 30,000 gallons. | 50 |
| Exceeding 30,000 gallons but not exceeding 40,000 gallons, | 60 |
| Exceeding 40,000 gallons but not exceeding 50,000 gallons . | 70 |
| Exceeding 50,000 gallons | 100 |

6. The following distances shall be kept clear at all times between protected works and a storage shed or an enclosure wall used for the storage of non-dangerous petroleum only:-

| Exceeding 5,000 gallons but not exceeding 10,000 gallons. | 15 |
| --- | --- |
| Exceeding 10,000 gallons but not exceeding 50.000 gallons. | 20 |
| Exceeding 50,000 gallons. | 30 |

7. The distances specified in conditions 5 and 6 may be reduced by the licensing authority in cases where screen walls are provided or other special precautions taken or where there are special Circumstances that, in his opinion, warrant the reduction.

8, Drums or other receptacles containing petroleum shall only be opened in the licensed premises and for the time necessary for drawing off the petroleum, and during such drawing off every reasonable precaution shall be adopted for preventing the escape of petroleum or the vapour therefrom.

9. All empty receptacles which have contained dangerous petroleum sha11, except when they are opened for the purpose of cleaning them and rendering them free from petroleum vapour, be kept securely closed unless they have been thoroughly cleaned and freed from petroleum and inflammable vapour.

10. No person shall repair or cause to be repaired any receptac1e in which, to his knowledge, any petroleum is or has been kept until he has taken all reasonable precautions to ensure that the receptacle has been rendered free from petroleum and any inflammable vapour.

Provided that this condition shall not be deemed to prohibit the usual soldering operations connected with the filling and dispatching of petroleum receptacles when such operations are conducted in an approved place outside the storage shed.

11. Adequate precautions shall be taken at all times for the prevention of accident by fire or explosion.

12 Every care shall be taken to prevent any petroleum escaping into any drain, sewer, harbour, river or water course.

13. Adequate precaution shall be taken to prevent unauthorized persons having access to any petroleum kept and to any receptacles which contain or have contained petroleum,

14. Any accident, fire or explosion occurring within the licensed premises, which is attended with loss of human life or serious injury to person or property shall be reported to the nearest Magistrate or to the Officer-in-Charge of the nearest Police Station immediately and by telegraph or telephone where such means of communication are available.

15. Free access to the licensed premises, shall be given at all reasonable times to any Inspector or Sampling Officer and every facility shall be afforded to such officer for ascertaining that the rules and the conditions of this license are duly observed.

FORM ‘N’

[Article 7 of Schedule I]

License to store petroleum for specific work of national importance

License No…………………………					Fee Rs.…………….

License is hereby granted to ………………………………………..valid only for storage of the following kinds and quantities of petroleum in the licensed premises as per details shown in the approved plan attached hereto subject to the previsions of Petroleum Act, 1934 and the rules made there under and to the further conditions of this license.

Dangerous petroleum                                …………………………… gallons

Dangerous petroleum                                …………………………… gallons

Heavy petroleum                                       …………………………… gallons

Licensing Authority

This license shall remain into force till	………………………………………………

Description of the licensed premises		………………………………………………

Space for endorsement of renewal

| Date of renewal | Date of expiry | Signature of licensing authority |
| --- | --- | --- |

This license is liable to be cancelled if the licensed premises when inspected are not found conforming to the description and conditions attached hereto and contravention any of the rules and conditions, under which this license is granted, is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

CONDITIONS OF LICENSE

      - Petroleum shall be stored only in the storage shed, godown or pit as per details of the approved plan attached hereto.

      - The storage place shall not form part of, or be attached to any building in which any person resides or works or persons assemble for any purpose.

      - Any two storage places not more than 5 meters apart be deemed to be one storage place.

      - Every storage place shall be surrounded by a wall or fence of at least 2 meters in height.

      - The drum or other receptacle containing petroleum shall only be opened in the licensed premises for the time necessary for drawing off the petroleum, and during such drawing off every reasonable precaution shall be adopted for preventing the escape of petroleum or the vapor there.

      - Adequate precautions shall be taken at all times to prevent unauthorized persons having any access petroleum kept and any receptacles, which contain or have contained petroleum.

      - Adequate precautions shall be taken at all times for the prevention of accident by fire explosion.

      - Every care shall be taken to prevent any petroleum escaping any drain, sewer, harbor, river, watercourse or public road.

      - The licensee shall keep daily records and accounts of all receipts and issues of petroleum in such as the licensing authority may from time to time prescribe and shall exhibits his stock and records to an Inspector or Sampling Officer on demand.

      - Any accident, fire or explosion within the licensed premises causing loss of human life or serious injury to person or property shall be immediately reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station and by telegraph/fax or telephone to the Chief Inspector of Explosives (Telegraphic address; “Explosives, Karachi”).

      - Free access to the licensed premises shall be given at all reasonable times to any Inspector or Sampling Officer and every facility shall be afforded to any such officer ascertaining that the rules and conditions of this license are duly observed.

FORM ‘P’

[See rule 77]

License to transport petroleum in bulk on land by mechanically propelled vehicles

License No ………………………………			Fee Rs.……………...

License is hereby granted to …………………………………………to transport petroleum in bulk on land by the vehicle as described below subject to the provisions of the Petroleum Act, 1934, and the rules made there under and to the further conditions of this license.

This license shall remain valid up to the …………day of ……20……

Date of issue ……………………………………………

Licensing Authority

DESCRIPTION OF VEHICLE

(a)	Make and model		        ……………………………………

(b)	Engine number		        ……………………………………

(c)	Chassis number		        ……………………………………

(d)	Registration number		        ……………………………………

(e)	Name of the registered owner         ……………………………………

(f)        Name of carriage contractor            ……………………………………

(g)	Total number of compartments       ……………………………………

(h)	Capacity of each compartment        ……………………………………

(i)	Class(es) of petroleum authorized

to be carried in the vehicle               ……………………………………

This license is liable to be cancelled if the licensed premises when inspected are not found conforming to the description and conditions attached hereto and contravention any of the rules and conditions, under which this license is granted, is also punishable with fine which may extend to five hundred rupees for a first offence and which may extend to two thousand rupees for any subsequent offence.

CONDITIONS OF LICENSE

      - The license or its authenticated copy shall at all times be kept in the licensed vehicle and produced on demand by an Inspection Officer.

2.	Only reasonable persons who are conversant with the conditions of this license shall be employed for driving the licensed vehicle or attending to it.

3.	The licensed vehicle shall be constantly attended to by a responsible person and by at least two persons while it is transporting petroleum;

Provided that the licensed vehicle, if its tanks and compartments are empty, be left un-attended in a place approved for the purpose, in writing by the Chief Inspector.

4.	The licensed vehicle shall at all times carry;

  - A portable fire-extinguisher of capacity not less than 9 liters and suitable for extinguishing oil fires; the extinguisher shall be kept unlocked at an easily accessible position which shall be away from the discharge faucets of the vehicle;

(b)	A separated oil-tight and electrically continuous hose with coupling to match the discharge faucet of the licensed vehicle and the inlet pipe into which the petroleum carried in the vehicle is to be unloaded; and

(c)	A flexible cable for electrical bonding; the cable shall be at least 5 meters long and shall have at each end a suitable clamp or clip.

5.	The licensed vehicle shall not be loaded or unloaded except in a place approved for the purpose, in writing, by the Chief Inspector.

Provided that the licensed vehicle may be unloaded at any other place with all due precautions and under adequate supervision if such unloading is necessitated due to an accident or breakdown.

  - Petroleum carried in the licensed vehicle shall not be directly transferred into any container or into the fuel tank of any motor conveyance or an internal combustion engine.

7.	The licensed vehicle shall not be loaded if any tank or compartment, pipe, valve, emergency discharge control of any safety fitting become leaky, defective or otherwise insecure until necessary reapers have been carried out satisfactorily and in the event of any leak in the tanks or compartments, until the leak is thoroughly repaired and all the tanks or compartment’s are tested hydrostatically to a pressure of 0.316 kg/sq.cm for a duration of not less than one hour and found satisfactory.

8.	Before petroleum is loaded into or unloaded from the licensed vehicle;

  - its engine shall be stopped and the battery shall be isolated by a proper switch or otherwise;

  - its wheel shall be secured by brakes or by scotching and in the case of animal drawn vehicles, animal shall be unhitched and removed;

  - A reasonable persons shall be in attendance and remain so until load or from which it is to be unloaded or loaded;

  - The correct filling or discharge hose shall be selected and connected by oil tight coupling at both ends; and

  - A reasonable person shall be in attendance and remain so until loading or unloading is over and the tanks and compartments have been sealed.

9.	Except when called upon by traffic signals or required by an Inspector of Explosives or a Sampling Officer, the licensed vehicle shall not stop on any road, congested area or a place, which is not, a place approved in writing under these rules for the loading, unloading or stabling of such vehicle.

    - No smoking and no fire or artificial light or any article capable igniting inflammable vapor shall be allowed on the licensed vehicle.

    - The licensed vehicle shall not be used for carrying passenger or any article-other than petroleum.

    - The licensed vehicle shall not be allowed to be repaired welding, soldering, brazing or hot riveting until its tanks. Compartment’s pipe and valve have been thoroughly cleaned and examined by a competent person and certified by him in writing to be free from inflammable vapor or oil.

    - No alteration in the licensed vehicle or its safety fitting shall be carried out without the previous sanction in writing of the licensing authority. Such alteration so sanctions so sanctioned shall be endorsed on this license by an amendment.

    - Every facility shall be given at all reasonable times to any Inspector or Sampling Officer for ascertaining that the rules and the conditions of this license are duly observed or for drawing samples.

    - Causing loss of human life or serious injury to person or property shall be immediately reported to the nearest Magistrate or to the Officer-in-charge of the nearest Police Station and by telegraph/fax or telephone to the Chief Inspector of Explosives (Telegraphic address; “Explosives, Karachi”).

SCHEDULE III

METHODS OF TESTING PETROLEUM

Determination of Flashing Point.

(See Rules 157 and 60)

  - APPARATUS TO BE USED.

The flashing point of petroleum and petroleum mixtures which are fluid at 50º F and which flash not above 120º F shall be determined by the Abel apparatus as hereinafter defined.

The flashing point of petroleum and petroleum mixture which are solid   at 50º F and which flash not above 120º F   shall be determined by the Abel apparatus, the test being modified as hereinafter described.

The flashing point of petroleum and petroleum mixtures which flash above 120º F, shall be determined by the pensky-mattens apparatus as hereinafter defined.

II.   PREPARING THE SAMPLES FOR TEST.

About ten fluid ounces of the sample, sufficient for three tests, should be transferred from the bottle into which the sample has been drawn to a pink flask or bottle, which should be immersed in water artificially cooled until a thermometer introduced into the sample, indicates a temperature not exceeding 50 degree F.

III (1) ABEL APPARATUES.

The apparatus to be employed shall be the Abel petroleum testing apparatus modified by having an oil cup provided with a stirrer. It shall be constructed to the dimensions herein specified within the limits of accuracy prescribed by the tolerances set forth below.

Oil Cup. --- The oil cup consists of a cylindrical vessel open at the top and fitted on the outside with a flat circular flange projecting at right angles.

Within the cup, fixed through the wall and silver soldered or brazed in place, there is a gauge consisting of a piece of wire bent upward and terminating in a point.

Material. --- Brass or gun-metal.

|  | Diminution | Tolerance |
| --- | --- | --- |
| Cup, wall and bottom thickness. | 17 I. W. G. | --- |
| Cup, internal distance. | 2 in. | + 0.05 |
| Cup, internal depth. | 2.2 in. | + 0.05 |
| Flange thickness. | 17 I. W. G. | --- |
| Flange, width. | O.5 in. | + 0.05 |
| Flange, distance of upper side from top edge of cup. | 0,375 in | + 0.05 |
| Gauge, thickness not less than. | 101 W.G. | --- |
| Gauge, distance of point from level of upper edge of cup. | 0.7 in. | + 0.005 |

Cover.---	The cup is provided with a close-fitting cover with a downward projecting rim barely reaching the flange  on the cup.  The downward projecting rim is made solid with the top or silver soldered or brazed in place.  Upon the cover are mounted a thermometer socket, trunnion to support oil test lamp a pair of guides in which a slide moves, and a white bead.  The top of the cover is pierced by three rectangular holes symmetrically placed on a diameter, one in the center and the other two as close as practicable to the inner sides of the cover rim and opposite each other.  These three holes are covered or uncovered by means of a slide moving in suitably disposed guides.  The slide has two perforations, one corresponding in all particulars to the center hole in the cover and the other to one of the holes at the side.  The movement of the slide is restricted by suitable stops, and its length and the disposition of the holes are such, that at the outer extremity of the movement of the slide, the holes in the cover are simultaneously just completely opened and at the inner extremity of the movement of the slide they are completely closed

The trunnions supporting the test lamp are fixed on the top of the guides and the lamp is mounted in the trunnions so that it is free to oscillate.  The lamp is provided with a jet to contain a wick and is so arranged that when the slide is moved so as to uncover the holes, the oscillating lamp is caught by a pin fixed in  the slide and tilted over the central hole in such a way that the lower edge of the cover bisects the circle formed by the bore of the jet when in the lowest position.  The flame then occupies a central position within the hole in both directions.

A suitably mounted gas-jet may be substituted for the lamp.

Dimension.     Tolerance.

Cover, thickness.						0.05 in.	+0,015

Cover, central hole, length (in direction of slide)		0.5 in		+0.005

Cover, central hole, width.					0.4 in		+0.005

Cover, peripheral holes, length (in direction of slide)	0.2 in 		+0.005

Cover, peripheral holes, width.				0.3 in 		+0.005

Slide, thickness						20 I.W.G.	-

Slide, width of supper  surface				0.5 in.		+0.01

(excess only)

Lamp, overall length of jet.				Approx. 0.6 in

to suit the      requirements for the position

of the jet

when tilted

Lamp, bore of jet at end.					0,0625 in	+0.005

Bead, diameter						0.15 in		+0.01

Thermometer Socket.

Internal diameter.	   	                                                 0.6 in		+0.01

Length of short slide measured from under surface of cover.    Approv o.5 in.  –

Length of long side measured from  under surface of cover.     Approv 0,75 in.  –

These dimensions are subject to the correct placing of the

thermometer when in position.                              			-	   -

Vertical depth of lowest part of thermometer below center of

under side of cover.						   1.5 in.	  + 0.1

The thermometer socket is in form of a split tube, mounted on a diameter at right angles to the diameter through the center of the holes, and fitted at such an angle as to bring the bulb of the thermometer, when in place, vertically below the center of the cover and at the correct distance from it.

A white bead, the dimensions of which represent the size of test flame to be used, is mounted in a visible position on the cover.

Materials.--- All parts excepting bead, brass of gun-metal. Bead, ivory or other suitable material.

Cover fitted with stirrer.--- Provision may be made in the cover for the reception of a stirrer which projects into the oil cup, for use with viscous materials only.

A bush is mounted on the cover in a position diametrically opposite the thermometer mounting, and its length is such and it is set at such an angle that the stirrer rod clears the oil-level gauge and the blades operate below the level of, and without fouling, thermometer  bulb.  The bush as placed as near as practicable to the outer edge of the cover.

Dimension	Tolerance. in.

Stem, length,overall. 						4 in.		       +0.1

Stem, length, lower end to  point of attachment of blades.     Approx. o.1 in.          –

Stem, length, lower end to upper surace of collar.		1.9 in.. 	        +0.1

Stem, length, upper surface of collar to lower end of thread.  2 in.		        +0.1

Stem diameter.						Approx. o.125 in.        –

Stem diameter collar.						Approx. o.25 in            -

Stem,   thread.							7 B .A.                          -

Blades  thickness.						17 I.W.G.                      –

Blades, length   excluding root. 				O.5 in.		            + 0

Blades breath  (all corner of blades rounded)			0,3125 in                  + 0.01

Blades, angle.							Approx. 45 degree.

Sleeve, length.							To suit stem giving

free rotation with

no appreciable verti-

cal play when screwed home.

Diameter of bore.						Sliding fit on stem.

Diameter of collar.						Approx. 0.25 in.              –

The stirrer consists of a round stem having four blades or vanes silver soldered in place at one end.  A collar is fixed on the stem so that when the stem is inserted into the bush from below, it is arrested at a position such that the correct length protrudes in the oil cup.  The top end of the stem is reduced and screwed.

A long sleeve having an internally screwed, knurled knob soldered to its upper end is passed over the upper end of the stem and screwed home.  The length of the sleeves is such that a flat faced collar at its lower end just comes into contact with the upper end of the bush, leaving the stirrer free to rotate without appreciable vertical play.

A flat headed cylindrical plug is provided for insertion in the bush when the stirrer is not is use.

Material.--- Brass  or gun metal.

Heating vessel.--- The heating vessel or bath consist of two  flat bottomed cylindrical copper vessels placed coaxially one inside the other and soldered at their tops to a flat copper ring, greater in outside diameter than the larger vessel and of smaller inside diameter that the smaller vessel.  The space between the two vessels is thus totally enclosed and is used as a water jacket.

Dimension.         Tolerance.

In

Inner vessel, thickness.					24 I.W.G. 	             -

Inner vessel,internal diameter.				3 in.			+0.05

Inner vessel, internal depth.					2.5 in.			+0.05

Outer vessel, thickness, not less  than	 			24 I.W.G.		 -

Outer vessel internal  diameter  				5.5 in.			+ 0.1

Outer vessel internal   depth					5.75 in 		+ 0.1

Top plate, thickness, not less than.				20 I.W.G.		-

Top plate, outer flange projection.				0.375 in		+ 0.1

Top plate, diameter of central hole				To suit ebonite or store

fibre ring, clearance not

to exceed 0.1 in.

Ebonite or fibre ring, internal diameter.			Easy fit on oil cup.          –

Ebonite or fibre ring, external diameter of flange.		2.75 in			+ 0.2

Ebonite or fibre ring, overall depth of spigot			0,25 in			+ 0.2

Ebonite or fibre ring, thickness flanage and spigot.		0.08 in.		+0.005

# Ebonite or fibre ring, screw, C.S.				S.B.A. x 0.15 in          _

Thermometer socket, internal diameter.			0.6 in.			+ 0.1

Thermometer socket, height from top of plate.		0.75 in			+ 0.1

An ebonite or fiber ring of right-angle section is fitted into the hole in the center of the flat ring forming the top of the bath and when the apparatus is in  use, the oil cup fits into, and its flange rests upon, this ebonite or fiber ring so that the oil cup is centrally disposed within the heating vessel.  The ebonite or fiber ring is secured in place by means of six small screws having their heads sunk below the surface of the ring, to avoid metallic contact between the bath and the oil cup.

A spite socket, similar to that on the cover of the oil cup, but set vertically, allows a thermometer to be inserted into the water space.  A funnel and overflow pipe also communicate with the water space through the top plate and two loop-handles are provided thereon.

The bath rests upon a cast-iron tripod strand, to the ring of which is attached a cylindrical copper jacket not less than 24 I.W.G.  flanged inwards at the top, and of such dimension that the bath, while resting firmly on the iron ring, just  touches with its outward projecting flange the inward turned flange of the jacket.  Two handles are provided on the outer jacket.

Diameter of the outer jacket 6.5 inches x 0.1 inch.

Spirit lamp.--- A spirit lamp is  provided for raising the temperature of the water bath, but any other suitable means may be employed for this purpose.

Thermometers. ---  Two thermometers are provided, the one for ascertaining the temperature of the bath, the other for determining of flashing point.

OIL CUP THERMOMETER

Type 	    Mercury in glass, nitrogen filled, graduated on the stem enamel back.

Length.	    Approximately 9  inches.

Stem.	    Diameter 0.24 to 0.28 inches.

Bulb.		    Spherical, made of normal glass approved by the Board of Trade.

Diameter. 0.35 inch + 0.05

Range.	50 to 150  F with  expansion chamber.  Distance from the bottom of the   bulb    to the 50º line  2.75 inches to 3.15 inches   Distance from the 50º line to the 150º line, not less than 4.75 inches..

Immersion.	A swelling is made in the stem to ensure that the thermometer shall be fixed in its brass collar so that the distance from the top of the collar to the bottom of the bulb is 2.4 inches. + 0.05 inch.

Graduation.	Scale graduated in 1º F divisions every 5º and every 10º to be indicated by longer lines, figured at every 10º in full.

Marking.	     “Abel Oil Cup.”  Identification number, Fahrenheit; makers or vender’s name or trade mark.

WATER  BATH  THERMOMETER.

Type 	   Mercury in glass, nitrogen filled, graduated on the stem enamel back.

Length.	   Approximately 9  inches.

Stem.	     Diameter 0.24 to 0.28 inches.

Bulb.		     Cylindricxal,, made of normal glass approved by the Board of Trade.

Length  approximately 0,8 inch.  Diameter not to exceed the diameter of the stem.

Range.	     90º to 190º F with expansion chamber.  Distance from the bottom of  the   bulb to the 90º line 3.95 inches to 4.35 inches   Distance from the 90º line to the 190º line, not less than 3.55 inches..

Immersion.	A swelling is made in the stem to ensure that the thermometer shall be fixed in its brass collar so that the distance from the top of the collar to the bottom of the bulb is 3.5 inches. + 0.01 inch.

Graduation.	Scale graduated in 1º F divisions every 5º and every 10º to be indicated by longer lines. Figured at every 10º in full.

Marking.	      “Abel Water Bath.”  Identification number, Fahrenheit; makers or vender’s name or trade mark.

The brass collar of the thermometer is in each case  of the following dimensions:--

Outer diameter-   push fit in socket.

Thickness of tube –   22  I.W.B.

Trhickness of  flange – 0.1 inch. + 0,001 inch.

III  (II)  METHOD.

- For petroleum flashing below 90ºF.

The test apparatus shall be placed for use in a position where it is not exposed to currents of air or draughts.

The heating vessel or water-bath shall be filled by pouring water into the funnel until it begins to flow out at the spout of the vessel.  The temperature of the water at the beginning of the test shall be 130º F and not heat shall be applied to the water-bath during the test.  When a test has been completed and it is desired to make another test the water-bath shall be again raised to 130º F, which may conveniently be done while the petroleum cup  is being  emptied, cooled and refilled with a fresh sample to be tested.  The next test is then proceeded with.

If an oil test lamp is being used it shall be prepared by fitting it with a piece of flat plaited candle wick and filling it with colza or rape oil up to the lower edge of the opening of the spout or wick tube.  The lamp shall be trimmed so that when lighted it gives a flame of about 0.15 of an inch diameter, and this size of flame, which is represented by the projecting white bead on the cover of the oil-cup is readily maintained  by  simple manipulation from time to time with a small wire trimmer.  A gas test flame may be employed, and if so, the size of the jet of flame shall be adjusted to the size laid down above.

The bath having been raised to the proper temperature, the cup shall be placed on a level surface in a good light and the oil to be tested shall be poured into it, until the level of the liquid just reaches the point of the gauge which is fixed in the cup.  Before a test is begun the temperature of the oil shall be determined and shall be brought to approximately 60º F.  The cover, with the slide closed, shall then be put on to the cup and pressed down so that its edge rests on the rim of the cup, and the cup shall be so placed into the bath or heating vessel, every care being taken  to avoid wetting the sides of the cup with the oil.  The thermometer in the lid of the cup has been adjusted so as to have the correct immersion when the brass collar of the thermometer is properly seated , and its position shall not in any circumstances be altered.  When the cup has been placed in the proper position, the scale of the thermometer faces the operator.

The test-lamp shall then be placed on position upon the lid of the cup.  When the temperature has reached 60º F, the operation of testing shall be begun, the test flame being applied once for every rise of one degree, in the following manner:-

The slide shall be slowly drawn open while a metronome, set at 75 to 80 beats per minute, beats three times and shall be closed during the fourth beat.  A pendulum of 24 inches effective length may be used in place of the metronome, counting one beat from one extremity of the swing to the other.

The barometric pressure shall be observed and recorded.  No correction shall be made except in case of dispute, when the flashing-point figure shall be corrected according to the following rule:-

For each inch (2522.4 mm) below 29.92 in (760 mm) barometric reading add 1.6º F to the flashing-point.

For each inch (25.4 mm) above 29.92 in. (760 mm) barometric reading, subtract 1.6º F. from the plashing point.

- For petroleum flashing between 90ºF and 120º F.

The air chamber which surrounds the oil cup shall be filled with cold water at a depth of 1.5 inch and the heating vessel or water bath filled at usual, but also with cold water.  The lamp shall then be placed under the apparatus and kept there during the entire operation, and the temperature of the oil raised at the rate of 2º F to 2.25ºF  per minute, the testing being carried out as laid down in the previous section, except that the test flame shall first be applied  when the temperature has reached 80º F.

- For solid petroleum mixtures.

Solid petroleum mixtures are to be tested in the Abel apparatus in the following manner:-

The solid mixture must be cut into cylinders 1.5 inch long and 0.25 inch in diameter by means of a cork borer of other similar cutter having the correct internal diameter.  These cylinders are to be placed in the petroleum cup of the testing apparatus in a vertical position in such number as will completely fill the cup.  The cylinders must be in contact with one another, but must not be so tightly packed as to be deformed in shape.

Five or six of the cylinders in the center of the cup must be shortened to 0.5 inch to all space the thermometer bulb.

The air bath of the testing apparatus must be filled to a depth of 1.5 inch with water.  The water bath must then be raised to, and maintained at a temperature of about 80º F.

The cup must then be placed in the air bath, and the temperature of the sample must be allowed to rise until the thermometer in the oil cup shows 75ºF, when the test flame must be applied.

If no flash obtained, this temperature must be maintained constant in the oil-cup for one hour, at the expiration of which time the test flame must again be applied.

If flash is obtained, the solid mixture will be subject to the provisions of the Petroleum Act, 1934.

Note. – It may, in many cases, save time in testing samples of petroleum mixtures to apply the test flame after the sample has been a few minutes in the cup and while still at the temperature of the room in which the test is being carried out, provided that this temperature is below 76 degree F.  If a flash is obtained by this means, it is unnecessary (for the purpose of the Petroleum Act) to proceed with the test at a higher temperature.

- (1) THE PENSKY MARTENS APPRATUS.

The standard Pensky-Martens Closed Tester shall be used for determining

the flashing point of petroleum products having a flashing point above 120º F.

Every instrument shall be marked with the letters I.P.T., an identification number (on the cup, cover and top plate) and the name of the maker or vendor, such stamping implying a guarantee that the instrument complies with the requirements specified below.

The Pensky Martens Tester shall include the following major parts:-

Cup. – The cup of the standard Pensky-Martens Tester shall be made of brass and shall satisfy the following dimensional specification:-

THE PENSKY MARTENS CLOSED TESTER.

Dimension.                                                              Inches.	  Inches.

Inside diameter below filling mark.				  2.000		+ 0.050

Difference, inside and outside diameters below filling mark.   0.125            + 0.010

Inside height.							               2.200	+ 0.050

Thickness of bottom						               0.095	+ 0.025

Distance from rim to filling mark.				   0.860	+ 0.015

Distance lower surface flange to bottom of cup.		   1.795	+ 0.015

The inside of the cup may be turned to a slightly larger diameter above the filling mark and the outside may be tapered above the flange, but the wall thickness  at the upper edge shall be not less  than 0.04 in.  The flange should be approximately 0.5 in wide and approximately 0.125 in thick.  It shall be equipped with devices for locating the position of the lid on the cup and the cup centrally in the stove.  A handle, attached permanently to the flange of the cup, is a desirable accessory,

NOTE;- If the bottom of the cup is affixed it shall be brazed or hard soldered.

Stirring device.---The lid shall be equipped with a stirring device consisting of a vertical steel shaft, not less than 0.1 in, nor more than 0.125 in. in diameter, mounted in the centre of the cup, carrying two bladed  brass propellers, and provided with any convenient means for operating. The blades of both propellers shall be approximately 0.3 in. wide and shall be set at an angle of approximately 45º.  The smaller (up per) propeller shall have an over-all diameter of approximately 0.75 in.  The larger (lower) propeller shall have an over-all diameter between 11.25 and 1.75 in.  The thickness of the propeller blades shall be not less than 0.48 in. not more than 0.08 in; which limits correspond respectively to No. 18 and 14 S.W.G.  The propeller blades shall be brazed or hard soldered to collars on the vertical shaft and the collars shall have horizontal and vertical dimensions not greater than 0.4 in.

The plane of the centre of the upper propeller shall be 0.4 in. below the level of the rim of the cup.  The plane of the centre of the lower propeller shall be 2.0 in. below the level of the rim of the cup.  The level of the rim of the cup is in effect the level of the plane part of the portion of the lower surface of the lid inside the rim.

Cover proper.--- The cover proper shall be of brass and shall have a rim projecting downward almost to the flange of the cup and fitting the outside of the cup closely.  The thickness of the cover, measured just inside the rim, shall be not less than 0.03 in. or more than 0.08 in. There shall be proper locating device engaging with a corresponding locating device on the flange of the cup.

There shall be four openings in the cover.

Opening A is an area defined by arcs of two concentric circles and the intersected lengths of two radii.  The radius of the outer circle shall be not less than 0.94 in. or more than 0.97 in. The chord of the arc of the outer circle shall be not less than 0.5 in. or more than 0.54 in.

Openings B and C are equal areas, each of the same general form as opening A but of approximately half the (angular) width. The radii of the defining inner and outer circles shall be within the limits specified for the radii of the two circles

Openings B and C shall be equally distant from opening A, and radii drawn through each of their centers shall be at an angle of not less than 135º nor more than 140º.

Opening A, B and C need not conform exactly to the shape of geometrical figures bounded by arcs of two concentric circles and intersected length of radii; Their boundaries must, however, fall on or between the lines indicated by the limiting values of the dimensional specification of the preceding text.

Opening D is a split tube to grip the thermometer collar.  It shall be set at an angle of not less than 10 º nor more than 15º from the perpendicular.  It centre is approximately 0.75 in. from the centre of the lid and on a radius at an angle of not less than 50º nor more than 60º from the radius passing through the opening C.  Its height shall be such that, when a standard thermometer is in position, the bottom of the bulb shall be 1.5 in; + 0.1  in. below the level of the rim of the cup (which corresponds to the lower surface of the portion of the lid inside the rim).

Shutter.- The lid shall be equipped with a brass shutter, approximately 0.1  in thick, operating on the plane of the upper surface of the lid.  The shutter shall be so shaped and mounted than it rotates on the surface of the lid about an axis normal to the lid, and through its centre, between two stops so placed that when in one extreme position the openings A, B and C of the lid are completely closed and when in the other extreme position these opening are completely opened.

Flame exposure device.- The tip of the flame jet shall have an orifice 0.027 in to 0.03 in. diameter.  The flame-exposure device shall be equipped with an operating mechanism which, when the shutter is in the “open” position, depresses the tip so that the centre of the orifice is between the plan of the under and upper surfaces of the lid proper, at a point on a radius passing through the centre of the larger opening A and approximately 0.1 in. from the outer edge of the opening.

The test flame shall be approximately spherical and shall be regulated to be of the same mean diameter as a bead 0.16 in, in diameter of some suitable material mounted on the lid.

The mechanism operating the shutter should be of the spring type and constructed so that when at rest the shutter shall completely close the three opening.  When operated to the other extreme the three openings in the lid shall be fully open and the tip of the exposure tube shall be fully depressed.

NOTE.- A pilot flame for automatic relighting of the test flame should be provided.

Where gas is not available, an oil burner shall be used as the test flame, the position of which shall correspond with that of the gas flame previously specified.

Stove.- Heat shall be supplied to the cup by means  of a properly designed stove which is equivalent to an air bath.  This stove shall consist of (i) an air bath and (ii) a top plate on which the flange of the cup rests.

Air bath:- The air bath shall have a cylindrical interior 1.625 in. to 1.66 in deep and a diameter not less than 0.125 in, nor more than 0.156 in. greater than the outside diameter of the cup, with the minimum clearance of 0.05 in.  The air bath shall be a flame-heated metal casting.

NOTE.-  The casting shall  be so designed and used that the temperature of bottom and wall is approximately the same.  On this account it should be not less than 0.25 in. thick.  The apparatus shall be designed so that products of combustion of the flame cannot come into connect with any part of the cup.

Top Plate.- The top plate  shall be of metal.  The total distance from the upper surface of the plate to the bottom of the air bath shall exceed the distance from the under-surface of the flange to the bottom of the cup by not less than 0.063 in. nor more than 0.125 in.

The top plate shall be mounted with an air gap between it and the air bath.  The top plate may be attached to the air bath by means of three screws and spacing bushings.  The spacing bushings shall be of proper thickness to define the air gap which shall be not less than 0.125 in. nor more than 0.187 in.  The spacing bushings shall be not more than 0.37335 in. in diameter.

Thermometers.- A low range thermometer shall be used with the Standard Pensky-Martens Tester for determining the flashing-point above 120o F. The thermometer shall comply with the specification given below.

The thermometers shall conform to the following general specification:-

Type.- Mercury in glass, except where otherwise stated, Engraved stem. Nitrogen filled.

Stem.- The stem  shall be made of lead glass or other suitable glass.  Enamel back.

Bulb.- The bulb shall be made of a suitable thermometric glass approved by the National Physical Laboratory.  At present these glasses are:-

Identification mark.             Approved for

temperature

up to.

Normal glass made by James Powell and

Sons, Ltd                                                             Single blue stripe.	350 º C

Normal glass made by Frank Tolmey and

Co. Ltd.                                                               Two blue stripes.	350 º C

Normal glass, Jena iii made by Schotta

And  Genossen.                                                    Purple stripe 	350 º C

Corning Borosilicute made by Corning

Glass Co.                                                             Blue and red stripe 	359 º C

Corning Borosilicate made by Corning

Glass Co.                                                               	450 º C

Jena 59 iii made by Schott and Geempssem/                                             450 º C

Jena 2954  made by Schott and  Genossen.            Single black stripe.	450 º C.

Expansion and contraction chambers.- No contraction chamber shall be above the immersion line and no enlargement of the bore shall be within 10 mm. of the immersion line or of any part of the scale.

-------------------------------------------------------------------------------------------------------------

Graduation and figuring.- The graduation lines shall be clearly etched, and of uni8form thickness not exceeding 0.15 mm. The lines shall all at right angles to the axis of the thermometer.  When thermometer is viewed from the front and in a vertical position the lines shall all finish on a line parallel to the axis on the left hand side.  Certain of the graduation lines shall be extended on the right hand side but the shortest graduations shall not extend across the bore.  When the diameter of the tub e permits the figures shall be upright when the thermometer is viewed from the front and in a vertical position, and should preferably be placed to that they would be intersected by the line to which they refer if it were extended.

Marking.- In addition to the special markings given in the table, each thermometer shall be marked with an identification number, and the marker’s or vendor’s name or trade mark:-

Name and special marking.		                       “ I.P.T.P.M.  Low.”

Dimension-Stem, diameter.				                             6 – 7  mm

Bulb, shape						                              Round.

Bulb length.

Bulb diameter.						                               8 mm max.

Overall length, + 5 mm				                               275 mm

Length of graduated portion.				                   150-180 mm

Distance, bottom of bulb to 20o mark		                               70-85 mm

Range.							                                20 º F to 230 º F

Graduation.						                                 1 º F

Longer lines at each.					                                 5 º F  and 10 º mF.

Figured at each/					                                          10 º F

Expansion chamber.					                                 Required.

Immersiod	 		 			                                           2.2 in.

Top finish.						                                            Glass ring.

Each thermometer shall be mounted securely in a thermometer collar so that from the under-side of this collar to the bottom of the bulb the distance is 2.1 in.  (+ 0.05 in.)

The  thermometer collar shall have an outside diameter of 0.5 in;  + 0.002 in  and a flange 0.1  in;  + 0.01 in.   in thickness. The cement used to fasten the thermometer into the collar shall be of such a nature that it will withstand the action of oil cup to the highest temperature at which the thermometer is used.

Drying of the sample,

If gas oil or fuel oil is being tested the sample shall be dried by the following method:-

One hundred grams of well-dried granular calcium chloride is placed in a dry wide mouth stopper glass bottle.

Two hundred and fifty milliliters of the oil is then poured upon the calcium chloride.  The stopper is secured in position by tying.  The bottle is then well shaken and is stood in a vessel of water, the level of the water being up to about one-third of the height of the oil in the bottle.  The water is next raised to a temperature of 50 º C. (120 º F) and is maintained at the temperature for a period of seven hours, the bottle and its contents being well-shaken up at  intervals of about an hour.  At the end of this treatment the bottle and its contents are allowed to cool to atmospheric temperature; the bottle is then opened and sufficient of the oil for test filtered through paper on a Buchner funnel.

- (II) METHOD.

All parts of the cup and its accessories shall be thoroughly clean and dry before starting the test.  Particular care should be taken to avoid the presence of any gasoline or naphtha used to clean the apparatus after a previous test.

The cup shall be filled with the oil to be tested up to the level indicated by the filling mark.

The lid shall be placed on the cup and the latter set in the stove.  Care should be taken to have the locating devices properly engaged.  The thermometer shall be inserted.

The test flame shall be lighted and adjusted so that it is of the size of a bead 0.16  in. in diameter.

Heat shall be supplied at such a rate that the temperature read on the thermometer increases not less than 9 or more than 11 degrees per minute.  The stirrer shall be turned at a rate of approximately 60 revolutions per minute.

Application of the test flame shall be made at each temperature reading which is a multiple of 2 º F, up to 220 º F.  For the temperature range above 220º F application shall be made at each temperature reading with is a multiple of 5 ºF the first application of the test flame shall be made at a temperature at least 50o F below the actual flashing-point.  Application of the test flame shall be made by operating the device controlling the shutter and test flame burner so that the flame  is lowered in one-half second,  left in its lowered position for one second, and quickly raised to its high position.  Stirring shall be discontinued during the application of the test flame.

The flashing point is taken as the temperature read on the thermometer at the time of the flame application that causes a distinct flash in the interior of the cup.  The true flash must not be confused with the bluish halo that sometimes surrounds the test flame for the applications preceding the one that causes the actual flash.

The barometric pressure shall be observed and recorded.  No correction shall be made except in case of dispute, when the flashing point figure shall be corrected according to the following rule:-

For each inch (25.4 mm) below 29.92 in. (760 mm) barometric reading add 1.6 º F to the   flashing point.

For each inch (25.4 mm) above 29.92 in . (760 mm) barometric reading subtracts 1.6 º F, from the flashing-point.

- THE FLASHING POINT.

If is flash takes place at any temperature below 76 º F, the temperature at which it occurs is noted.  Two fresh portions of the sample are then to be successively tested in a similar manner and the results recorded. If no greater difference than to degrees Fahrenheit exists between any two of the three recorded results and if in no instance the flash has taken place within eight degrees Fahrenheit of the temperature at which the testing was commenced, the avertable of the three readings gives the flashing-point recorded by that particular instrument, but without either apparatus correction or thermometer correction.  In the event of there being a greater difference than two degrees Fahrenheit between any two of the readings,  or if the flash has occurred within eight degrees of the temperature  at which the testing was commenced, the series of tests is to be rejected and a fresh series of three similarly obtained.

If, however, a flash has occurred  at or below 64 º F when the test was applied in the manner above  described, the next test shall be commenced 10 º F, lower than the temperature at which the flash had been previously obtained, and this procedure    shall be continued until the results of three consecutive tests do not show a greater  difference than two degrees Fahrenheit and until a flash has not occurred in any of the three tests within eight degrees Fahrenheit of the temperature at which the test was commenced.  Provided always that if at the commencement of the series of tests a flash has occurred on the first application of the test flame at 60 º F, and if a flash has also occurred on the first application of the flame in each of the three successive test in which the test flame is first applied at 60 º F, as above directed, the testing officer shall certify that the petroleum has a flashing point below 67 º F, and the sample shall be reported as “dangerous petroleum”.

If a temperature of 76 º F has been reached without a flash occurring the application of the test flame is to be continued at every degree rise of temperature until a temperature of 89 º F, has been reached.  If no flash occurs up to this point the test shall be continued on a fresh sample as in Section III (II) (2) above.

If no flash occurs up to 120 º F, the flashing point shall be determined by the Pensky-Martens apparatus and method, as described above.

SCHEDULE IV

(See rule 98A)

- Shops may be allowed where pump sites are located on highways and town main roads.

- Pump sites shall not be located on service road or near bus stand, hotel, school, Public Park and residential building.

- A minimum frontage and depth of pump site for shop shall not be less than 30 meters and 20 meters respectively.

- Shop shall be at least 10 meters away from the nearest fill point of dangerous petroleum storage tank and dispensing unit.

- Area of shop shall not be more than 15% of total covered area excluding canopy at the pump premises. A separate fee of rupees twenty five per square foot shall be charged for any additional area of shop.

- Entrance to shop shall be kept clear at all times.

- Shop floor shall not be more than half meter higher than outer ground floor.

- Storage tanks shall not be on the same side of shop.

- There shall be no opening from adjacent premises to a shop.

- Shop shall not be opened at any pump site without prior approval in writing of the Chief Inspector of Explosives.

- Roof of the shop shall not be used for any other purpose.

- Heaters, burners or any appliance likely to cause spark of petroleum vapours shall not be used inside a shop, however a micro-wave oven may be used.

- Seating arrangement for customers shall not be provided inside a shop’

- Only packed food items, cold drinks, souvenirs and medicines shall be stored. In case of other items permission of the Chief Inspector shall be obtained in writing.

- At least two fire extinguishers of 10 kgs, each shall be provided exclusively for shop.

- A separate fee of Rs. 5000/- per year or part thereof shall be paid for every facility which is not directly connected with storage and distribution of petroleum. (Provision of tyre puncture shop and car washing facilities are exempted)

Any arrangement not in conformity with these items which has already been permitted by the Department of Explosives shall be deemed to have been permitted by the Chief Inspector of Explosives.

***************************************